## Figure 1
Figure 1. VOS Calculation Table: economic value, load match, loss savings and distributed PV value
|  |  | Gross Value | X | Load Match Factor | X | (1+ | Loss Saving Factor | ) | = | Distributed PV Value
| 25 Year Levelized Value |  | ($/kWh) |  | (%) |  |  | (%) |  |  | ($/kWh)
Table
| Avoided Fuel Cost | 8 | GV1 |  |  |  |  | LSF-Energy |  |  | V1
| Avoided Plant O&M - Fixed | 9 | GV2 |  | ELCC |  |  | LSF-ELCC |  |  | V2
| Avoided Plant O&M - Variable | 10 | GV3 |  |  |  |  | LSF-Energy |  |  | V3
| Avoided Gen Capacity | 11 | GV4 |  | ELCC |  |  | LSF-ELCC |  |  | V4
| Avoided Reserve Capacity Cost | 12 | GV5 |  | ELCC |  |  | LSF-ELCC |  |  | V5
| Avoided Transmission Capacity Cost | 13 | GV6 |  | ELCC |  |  | LSF-ELCC |  |  | V6
| Avoided Dist. Capacity Cost | 15 | GV 7 |  | PLR |  |  | LSF-PKR |  |  | V7
| Avoided Environmental Cost | 17 | GV8 |  |  |  |  | LSF-Energy |  |  | V8
Avoided Voltage Control Cost
Solar Integration Cost
Value of Solar
* Gross Values are Calculated in Tables 8 - 17

## Table 1
Table 1. VOS components included in methodology
Value Component | Basis | Legislative Guidance | Notes
Avoided Fuel Costs | Energy Market Costs (portion attributed to fuel | Required (energy) | Includess cost of long-term price risk
Avoided Plant O&M Cost | Energy Market Costs (portion attributed to O&M | Required (energy)
Avoided Generation Capacity Costs | Capital cost of generation to meet peak load | Required (capacity)
Avoided Reserve Capacity Cost | Capital cost of generation to meet planning margins and ensure reliabitiy | Required (capacity)
Avoided Transmission Capacity Cost | Capital cost of transmission | Required (transmission capacity)
Avoided Ditribution Capacity Cost | Capital cost of distribution | Required (delivery)
Avoided Environmental Cost | Externality costs | Required (environmental)
Voltage Control | Cost to regulate distribution (future inverter designs) |  | future (TBD)
Integration Cost | Added cost to regulate system frequency with variable solar |  | future (TBD)
** VOS components included in methodology

## Table 2
VOS Components not included in methodology
Value Component | Basis | Legislative Guidance | Notes
Credit for local Manufacturing/Assembly | Local tax revenue tied to net solar jobs | Optional (Identified in legislation) | Includess cost of long-term price risk
Market Price Reduction | Cost of wholesale power reduced in response to reduction in demand
Disaster Recovery | Cost to restore local economy (requires energy storage and islanding inverters
**VOS components not included in methodology

## Figure 3
Figure ES-a. VOS Calculation Table: economic value, load match, loss savings and distributed PV value
|  |  | Gross Value | X | Load Match Factor | X | (1+ | Loss Saving Factor | ) | = | Distributed PV Value
| 25 Year Levelized Value |  | ($/kWh) |  | (%) |  |  | (%) |  |  | ($/kWh)
|  | Table |  |  | 3 |  |  | 3
| Avoided Fuel Cost | 8 | 0.03689 |  | 100% |  |  | 9.798% |  |  | 0.040504
| Avoided Plant O&M - Fixed | 9 | 0.0016166 |  | 48.56% |  |  | 10.75% |  |  | 0.0008694
| Avoided Plant O&M - Variable | 10 | 0.0015702 |  | 100% |  |  | 9.798% |  |  | 0.001724
| Avoided Gen Capacity | 11 | 0.044121 |  | 48.56% |  |  | 10.75% |  |  | 0.023728
| Avoided Reserve Capacity Cost | 12 | 0.0032208 |  | 48.56% |  |  | 10.75% |  |  | 0.0017322
| Avoided Transmission Capacity Cost | 13 | 0.028047 |  | 48.56% |  |  | 10.75% |  |  | 0.015084
| Avoided Dist. Capacity Cost | 15 | 0.015214 |  | 55.22% |  |  | 13.18% |  |  | 0.009509
| Avoided Environmental Cost | 17 | 0.026159 |  | 100% |  |  | 9.798% |  |  | 0.028722
Avoided Voltage Control Cost
Solar Integration Cost
[8 empty] | VOS Rate |  |  | 0.12187
The economic value, load match, distributed loss savings, and distributed PV value are combined in the
required VOS Levelized Calculation Chart. An example is presented in Figure 3 using the assumptions
made for the example calculation. Actual VOS results will differ from those shown in the example, but
utilities will include in their application a VOS Levelized Calculation Chart in the same format. For
completeness, Figure 4 (not required of the utilities) is presented showing graphically the relative
importance of the components in the example.
Having calculated the levelized VOS credit, an inflation-adjusted VOS can then be found. An EXAMPLE
inflation-adjusted VOS is provided in Figure 5 by using the general escalation rate as the annual inflation
rate for all years of the analysis period. Both the inflation-adjusted VOS and the levelized VOS in Figure
5 represent the same long-term value. The methodology requires that the inflation-adjusted (nominal)
VOS be used and updated annually to account for the current year’s inflation rate.
To calculate the inflation-adjusted VOS for the first year, the products of the levelized VOS, PV
production and the discount factor are summed for each year of the analysis period and then divided by
the sum of the products of the escalation factor, PV production, and the discount factor for each year of
the analysis period, as shown below in Equation ( 19 ).

## Table 18
Table 18. (Example) Calculation of inflation-adjusted VOS
Year | Analysis Period | Discount Factor | PV Production | Escalation Factor | Example VOS | Disc. Cost | Denom. in Equation 19 | Example VOS | Disc. Cost
|  |  | (kWh) |  | (Levelized) | ($) |  | (Inflation adj.) | ($)
2014 | 0 | 1 | 1451.6947 | 1 | 0.12187 | 176.9222 | 1451.6947 | 0.094815 | 137.6427 | 0.12187
2015 | 1 | 0.93888 | 1444.4362 | 1.0275 | 0.12187 | 165.278 | 1393.4449 | 0.097214 | 131.8368
2016 | 2 | 0.88149 | 1437.214 | 1.0558 | 0.12187 | 154.4002 | 1337.5325 | 0.099674 | 126.2759
2017 | 3 | 0.82762 | 1430.0279 | 1.0848 | 0.12187 | 144.2382 | 1283.8635 | 0.1022 | 120.9495
2018 | 4 | 0.77703 | 1422.8778 | 1.1146 | 0.12187 | 134.7451 | 1232.3481 | 0.10478 | 115.8478
2019 | 5 | 0.72954 | 1415.7634 | 1.1453 | 0.12187 | 125.8768 | 1182.8997 | 0.10743 | 110.9613
2020 | 6 | 0.68495 | 1408.6846 | 1.1768 | 0.12187 | 117.5922 | 1135.4354 | 0.11015 | 106.2809
2021 | 7 | 0.64308 | 1401.6412 | 1.2091 | 0.12187 | 109.8528 | 1089.8757 | 0.11294 | 101.7979
2022 | 8 | 0.60378 | 1394.633 | 1.2424 | 0.12187 | 102.6228 | 1046.1441 | 0.11579 | 97.504
2023 | 9 | 0.56687 | 1387.6598 | 1.2765 | 0.12187 | 95.8686 | 1004.1672 | 0.11872 | 93.3912
2024 | 10 | 0.53223 | 1380.7215 | 1.3117 | 0.12187 | 89.559 | 963.8746 | 0.12173 | 89.4519
2025 | 11 | 0.4997 | 1373.8179 | 1.3477 | 0.12187 | 83.6647 | 925.1988 | 0.12481 | 85.6788
2026 | 12 | 0.46915 | 1366.9488 | 1.3848 | 0.12187 | 78.1582 | 888.0749 | 0.12796 | 82.0648
2027 | 13 | 0.44048 | 1360.1141 | 1.4229 | 0.12187 | 73.0142 | 852.4406 | 0.1312 | 78.6033
2028 | 14 | 0.41356 | 1353.3135 | 1.462 | 0.12187 | 68.2087 | 818.2361 | 0.13452 | 75.2877
2029 | 15 | 0.38828 | 1346.5469 | 1.5022 | 0.12187 | 63.7196 | 785.4041 | 0.13792 | 72.1121
2030 | 16 | 0.36455 | 1339.8142 | 1.5435 | 0.12187 | 59.5258 | 753.8895 | 0.14141 | 69.0703
2031 | 17 | 0.34227 | 1333.1151 | 1.586 | 0.12187 | 55.6081 | 723.6395 | 0.14499 | 66.1569
2032 | 18 | 0.32135 | 1326.4496 | 1.6296 | 0.12187 | 51.9482 | 694.6032 | 0.14866 | 63.3664
2033 | 19 | 0.30171 | 1319.8173 | 1.6744 | 0.12187 | 48.5292 | 666.732 | 0.15242 | 60.6936
2034 | 20 | 0.28326 | 1313.2182 | 1.7204 | 0.12187 | 45.3353 | 639.9791 | 0.15628 | 58.1335
2035 | 21 | 0.26595 | 1306.6521 | 1.7677 | 0.12187 | 42.3515 | 614.2998 | 0.16023 | 55.6814
2036 | 22 | 0.2497 | 1300.1189 | 1.8164 | 0.12187 | 39.5641 | 589.6508 | 0.16429 | 53.3327
2037 | 23 | 0.23443 | 1293.6183 | 1.8663 | 0.12187 | 36.9602 | 565.9908 | 0.16844 | 51.0831
2038 | 24 | 0.22011 | 1287.1502 | 1.9176 | 0.12187 | 34.5277 | 543.2803 | 0.1727 | 48.9284
[6 empty] | 2198.0717 | 23182.6999 |  | 2152.1326
pg. 42-44:
To calculate the inflation-adjusted VOS for the first year, the products of the levelized VOS, PV
production and the discount factor are summed for each year of the analysis period and then divided by
the sum of the products of the escalation factor, PV production, and the discount factor for each year of
the analysis period, as shown below in Equation ( 19 ).
Equation 19
| InflationAdjusted VOS (0) = |  |  | SUM of (levelizedVOS*PVProduction(i)*DiscountFactor(i)) / SUM of (Escalation Factor (i)*PV Production(i)*DiscountFactor(i)
Once the first-year inflation-adjusted VOS is calculated, the value will then be updated on an annual
basis in accordance with the observed inflation-rate. Table 18 provides the calculation of the EXAMPLE
inflation-adjusted VOS shown in Figure 5. In this EXAMPLE, the inflation rate in future years is set equal
to the general escalation rate of 2.53%.

## Table 3
Table 3. Fixed Assumptions to be used for 2014 VOS Calculations - common to all utilities
Guaranteed NG Fuel Prices |  |  | Environmental Externalities
Year |  |  | Environmental Discount rate (real) | 3% | per year
|  |  | Environmental Discount Rate (nominal) | 5.833%
2014 | 4.5025 | $ per MMBTU | Environmental costs | (shown in separate table)
2015 | 4.258 | $ per MMBTU
2016 | 4.1986 | $ per MMBTU
2017 | 4.2727 | $ per MMBTU | Economic Assumptions
2018 | 4.3692 | $ per MMBTU | General Escalation rate | 2.75% | per year
2019 | 4.4936 | $ per MMBTU
2020 | 4.6893 | $ per MMBTU | Treasury Yields
2021 | 4.859 | $ per MMBTU | 1 year | 0.13%
2022 | 5.0028 | $ per MMBTU | 2 year | 0.29%
2023 | 5.0913 | $ per MMBTU | 3 year | 0.48%
2024 | 5.1458 | $ per MMBTU | 5 year | 1.01%
2025 | 5.2398 | $ per MMBTU | 7 year | 1.53%
|  |  | 10 year | 2.14%
NG fuel price escalation | 2.75% |  | 20 year | 2.92%
|  |  | 30 year | 3.27%
PV Assumptions
PV degradation rate | 0.5% | per year
PV life | 25 | years
** Fixed Assumptions to be used for 2014 VOS calculations - common to all utilities.
NG fuel price escalation (p.23)
For the Futures Market option, Guaranteed NG prices are calculated as follows. Prices for the first 12
years are based on NYMEX futures, with each monthly price averaged to give a 12-month average in $
per MMBtu. Prices for years beyond this NYMEX limit are calculated by applying the assumed annual
NYMEX price escalation. An assumed fuel price overhead amount, escalated by year using the assumed
NYMEX price escalation, is added to the fuel price to give the burnertip fuel price.
pg 7 The “Guaranteed NG Fuel Price Escalation” value of 4.77%, used as described later to calculate the
Avoided Fuel Costs, is calculated from a best fit to the listed NYMEX futures prices.
PV Assumptions (p.22)
PV degradation is accounted for in the economic calculations by reductions of the annual PV production
in future years. As such, the PV production in kWh per kW-AC for the marginal PV resource in year (i) is
given by:
Equation 12 (p.22)
[PV Production(i)] = [PV Production(0)] × (1 − PVDegradationRate)^(i)
where PVDegradationRate is the annual rate of PV degradation, assumed to be 0.5% per year – the
standard PV module warranty guarantees a maximum of 0.5% power degradation per annum.
PV Production (0) is the Annual Avoided Energy for the Marginal PV Resource.
Environmental Externalities (p. 22)
The Environmental Discount Rate is based on the 3% real discount rate that has been determined to be
an appropriate societal discount rate for future environmental benefits. As the methodology requires a
nominal discount rate, this 3% real discount rate is converted into its equivalent 5.61% nominal discount
rate as follows:
Nominal Discount Rate = (1 + Real Discount Rate) × (1 +General Escalation Rate) − 1
The EnvironmentalDiscountRate is used once in the calculation of the Avoided Environmental Costs in table 17.
Economic Assumptions (p.7)
Table 3 and Table 4 present fixed assumptions, common to all utilities and incorporated into this
methodology, that are to be applied to the calculation of 2014 VOS tariffs. These may be updated by
Commerce in future years as necessary when performing the annual VOS update. Table 4 is described in
more detail in the Avoided Environmental Cost subsection. Table terms can be found in the Glossary.
Published values from the Bureau of Labor and Statistics for the Urban Consumer Price Index (CPI)
(ftp://ftp.bls.gov/pub/special.requests/cpi/cpiai.txt) were used to calculate an average annual inflation
rate of 2.53% over the last 25 years (see equations below). This was taken as the expected general
escalation rate.
Equations 1 & 2 on pg 7
General Escalation Rate is equal to: |  | [(Nov2013CPI/Nov1988CPI)^1/(2013-1988)] - 1 = |  | [(224.939/120.300)^1/25] - 1 = |  | 2.535%
The General Escalation rate is used in table
Treasury Yields (p.21)
Similarly, a risk-free discount factor is given by:
Equation 9 (p.21)
Risk Free Discount Factor = 1/(1+ Risk Free Discount Rate
The RiskFreeDiscountRate is based on the yields of current Treasury securities12 of 1, 2, 3, 5, 7, 10, 20,
and 30 year maturation dates. The RiskFreeDiscountRate is used once in the calculation of the Avoided
Fuel Costs.
The Risk Free Discount Rate is used once in the calculation of the Avoided Fuel Costs in Table 8.

## Table 4
Table 4. Fixed environmental externality costs by year
Year | Analysis Year | CO2 Cost ($/MMBtu) | PN19 Cost ($/MMBtu) | CO Cost ($/MMBtu) | NOx Cost ($/MMBtu | Pb Cost ($/MMBtu) | Total Cost ($/MMBtu)
2014 | 0 | 2.1786 | 0.069 | 0 | 0.013 | 0 | 2.2606
2015 | 1 | 2.3007 | 0.071 | 0 | 0.013 | 0 | 2.3847
2016 | 2 | 2.4279 | 0.073 | 0 | 0.014 | 0 | 2.5149
2017 | 3 | 2.5603 | 0.075 | 0 | 0.014 | 0 | 2.6493
2018 | 4 | 2.6982 | 0.077 | 0 | 0.015 | 0 | 2.7902
2019 | 5 | 2.911 | 0.079 | 0 | 0.015 | 0 | 3.005
2020 | 6 | 3.0622 | 0.082 | 0 | 0.015 | 0 | 3.1592
2021 | 7 | 3.1464 | 0.084 | 0 | 0.016 | 0 | 3.2464
2022 | 8 | 3.3082 | 0.086 | 0 | 0.016 | 0 | 3.4102
2023 | 9 | 3.4764 | 0.089 | 0 | 0.017 | 0 | 3.5824
2024 | 10 | 3.6514 | 0.091 | 0 | 0.017 | 0 | 3.7594
2025 | 11 | 3.8333 | 0.093 | 0 | 0.018 | 0 | 3.9443
2026 | 12 | 4.0226 | 0.096 | 0 | 0.018 | 0 | 4.1366
2027 | 13 | 4.2193 | 0.099 | 0 | 0.019 | 0 | 4.3373
2028 | 14 | 4.4238 | 0.101 | 0 | 0.019 | 0 | 4.5438
2029 | 15 | 4.6364 | 0.104 | 0 | 0.02 | 0 | 4.7604
2030 | 16 | 4.8573 | 0.107 | 0 | 0.02 | 0 | 4.9843
2031 | 17 | 4.9908 | 0.11 | 0 | 0.021 | 0 | 5.1218
2032 | 18 | 5.2267 | 0.113 | 0 | 0.021 | 0 | 5.3607
2033 | 19 | 5.4718 | 0.116 | 0 | 0.022 | 0 | 5.6098
2034 | 20 | 5.7264 | 0.119 | 0 | 0.023 | 0 | 5.8684
2035 | 21 | 5.9908 | 0.123 | 0 | 0.023 | 0 | 6.1368
2036 | 22 | 6.2655 | 0.126 | 0 | 0.024 | 0 | 6.4155
2037 | 23 | 6.5507 | 0.129 | 0 | 0.024 | 0 | 6.7037
2038 | 24 | 6.8469 | 0.133 | 0 | 0.025 | 0 | 7.0049
**Fixed environmental externality costs by year
p. 39 The externality cost of CO2 emissions shown in Table 4 are calculated as follows. The EPA Social Cost of
Carbon (CO2) estimated for a given year is published in 2007 dollars per metric ton. These costs are
adjusted for inflation (converted to current dollars), converted to dollars per short ton, and then
converted to cost per unit fuel consumption using the assumed values in Table 16.
For example, the EPA externality cost for 2020 (3.0% discount rate, average) is $43 per metric ton of CO2
emissions in 2007 dollars. This is converted to current dollars by multiplying by a CPI adjustment factor;
for 2014, the CPI adjustment factor is of 1.12. The resulting CO2 costs per metric ton in current dollars
are then converted to dollars per short ton by dividing by 1.102. Finally, the costs are escalated using the
general escalation rate of 2.53% per year to give $50.77 per ton. Which equates to $51.22 per ton of
CO2, divided by 2000 pounds per ton, and multiplied by 117.0 pounds of CO2 per MMBtu = $2.970 per
MMBtu in 2020 dollars.
pg 40 - All pollutants other than CO2 are calculated using the Minnesota externality costs using the following
method. Externality costs are taken as the midpoint of the low and high values for the urban scenario,
adjusted to current dollars, and converted to a fuel-based value using Table 16.
For example, MN’s published costs for PM10 are $6,291 per ton (low case) and $9,056 per ton (high
case). These are averaged to be ($6291+$9056)/2 = $7674 per ton of PM10 emissions. For 2020, these
are escalated using the general escalation rate of 2.53% per year to $8,917 per ton. Which equates to
$8,917 per ton of PM10, divided by 2000 pounds per ton, multiplied by 0.007 pounds of PM10 per
MMBtu = $0.031 per MMBtu. Similar calculations are done for the other pollutants.
1

## Table 4a
Social Cost of Carbon (EPA)
|  | CO2 CostEPA (3.0%) | CPI Factor | Short ton | Escalation Factor | Escalated CO2 Cost Per Ton | CO2 Cost $/MMBtu
|  | $ per Metric Ton (2007) | $ per Metric Ton (Current) | $ per Ton | (%) |  | $/Mmbtu
2014 | 0 | 36 | 41.04 | 37.2414 | 1 | 37.2414 | 2.1786
2015 | 1 | 37 | 42.18 | 38.2759 | 1.0275 | 39.3284 | 2.3007
2016 | 2 | 38 | 43.32 | 39.3103 | 1.0558 | 41.5021 | 2.4279
2017 | 3 | 39 | 44.46 | 40.3448 | 1.0848 | 43.7656 | 2.5603
2018 | 4 | 40 | 45.6 | 41.3793 | 1.1146 | 46.1223 | 2.6982
2019 | 5 | 42 | 47.88 | 43.4483 | 1.1453 | 49.7602 | 2.911
2020 | 6 | 43 | 49.02 | 44.4828 | 1.1768 | 52.3459 | 3.0622
2021 | 7 | 43 | 49.02 | 44.4828 | 1.2091 | 53.7854 | 3.1464
2022 | 8 | 44 | 50.16 | 45.5172 | 1.2424 | 56.5497 | 3.3082
2023 | 9 | 45 | 51.3 | 46.5517 | 1.2765 | 59.4254 | 3.4764
2024 | 10 | 46 | 52.44 | 47.5862 | 1.3117 | 62.4165 | 3.6514
2025 | 11 | 47 | 53.58 | 48.6207 | 1.3477 | 65.5271 | 3.8333
2026 | 12 | 48 | 54.72 | 49.6552 | 1.3848 | 68.7617 | 4.0226
2027 | 13 | 49 | 55.86 | 50.6897 | 1.4229 | 72.1246 | 4.2193
2028 | 14 | 50 | 57 | 51.7241 | 1.462 | 75.6204 | 4.4238
2029 | 15 | 51 | 58.14 | 52.7586 | 1.5022 | 79.2539 | 4.6364
2030 | 16 | 52 | 59.28 | 53.7931 | 1.5435 | 83.0302 | 4.8573
2031 | 17 | 52 | 59.28 | 53.7931 | 1.586 | 85.3135 | 4.9908
2032 | 18 | 53 | 60.42 | 54.8276 | 1.6296 | 89.3454 | 5.2267
2033 | 19 | 54 | 61.56 | 55.8621 | 1.6744 | 93.5345 | 5.4718
2034 | 20 | 55 | 62.7 | 56.8966 | 1.7204 | 97.8864 | 5.7264
2035 | 21 | 56 | 63.84 | 57.931 | 1.7677 | 102.407 | 5.9908
2036 | 22 | 57 | 64.98 | 58.9655 | 1.8164 | 107.1022 | 6.2655
2037 | 23 | 58 | 66.12 | 60 | 1.8663 | 111.9782 | 6.5507
2038 | 24 | 59 | 67.26 | 61.0345 | 1.9176 | 117.0413 | 6.8469
CO2 | Technical Update of the Social Cost of Carebon for Regulatory Impact Analysis - Under Executive Order 12866, Appendix A
http://www.whitehouse.gov/sites/default/files/omb/assets/inforeg/technical-update-social-cost-of-carbon-for-regulator-impact-analysis.pdf
http://www.epa.gov/climatechange/EPAactivities/economics/scc.html
The Social Cost of Carbon
EPA and other federal agencies use the social cost of carbon (SCC) to estimate the climate benefits of rulemakings.
The SCC is an estimate of the economic damages associated with a small increase in carbon dioxide (CO2) emissions,
conventionally one metric ton, in a given year. This dollar figure also represents the value of damages avoided for a
small emission reduction (i.e. the benefit of a CO2 reduction).
The SCC is meant to be a comprehensive estimate of climate change damages and includes, but is not limited to,
changes in net agricultural productivity, human health, and property damages from increased flood risk. However,
given current modeling and data limitations, it does not include all important damages.
As noted by the IPCC Fourth Assessment Report, it is “very likely that [SCC] underestimates” the damages. The models
used to develop SCC estimates, known as integrated assessment models, do not currently include all of the important
physical, ecological, and economic impacts of climate change recognized in the climate change literature because of a
lack of precise information on the nature of damages and because the science incorporated into these models naturally
lags behind the most recent research. Nonetheless, the SCC is a useful measure to assess the benefits of CO2 reductions.

## Table 5
Table 5. VOS Data Table (Example Data) - required format showing example parameters used in the example calculations
Economic Factors | Input Data | Units |  | Power Generation | Input Data | Units
Start Year for VOS applicability | 2014 |  |  | Peaking CT, simple cycle
Discount rate (WACC) | 6.51% | per year |  | Installed cost | 640 | $/kW
|  |  |  | Heat rate | 9796 | BTU/kWh
Load Match (see calculation method)
ELCC(no loss) | 48.56% | % of rating |  | Intermediate peaking CCGT
PLR (no loss) | 55.22% | % of rating |  | Installed cost | 882 | $/kW
Loss Savings - Energy | 9.798% | % of PV output |  | Heat rate | 6777 | BTU/kWh
Loss Savings - PLR | 13.18% | % of PV output
Loss Savings - ELCC | 10.75% | % of PV output |  | Other
|  |  |  | Solar-weighted heat rate (see calculation method) | 6950.164 | BTU per kWh
PV Energy (see calculation method) |  |  |  | Fuel Price Overhead | -0.04 | $ per MMBtu
First year annual energy | 1451.6947 | kWh per kW-AC |  | Generation life | 35 | years
|  |  |  | Heat rate degradation | 0.1% | per year
Transmission (See calculation method) |  |  |  | O&M cost (first year) - Fixed | 2.0045 | per kW-yr
Capacity-related transmission capital cost | 40.7161 | $ per kW-yr |  | O&M cost (first year) - Variable | 0.0013539 | $ per kWh
|  |  |  | O&M Escalation Rate | 1.66% | per year
|  |  |  | Reserve planning margin | 7.3%
Distribution
|  |  |  | Capacity-related distribution capital cost | 335.7197 | $ per kW
|  |  |  | Distribution capital cost escalation | 2% | per year
|  |  |  | Peak load | 7284 | MW
|  |  |  | Peak load growth rate | 1.141% | per year
** VOS Data Table (EXAMPLE DATA) -- required format showing example parameters used in the example calculation
Discount Rate (WACC) determined from most recent rate case
a Discount rate of 8% is used in the example for Tables 9-13, and 15.
Load Match Factor (p. 17 - 18)
Capacity-related benefits are time dependent, so it is necessary to evaluate the effectiveness of PV in
supporting loads during the critical peak hours. Two different measures of effective capacity are used:
Effective Load Carrying Capability (ELCC)
Peak Load Reduction (PLR)
Near term PV penetration levels are used in the calculation of the ELCC and PLR values so that the
capacity-related value components will reflect the near term level of PV penetration on the grid.
However, the ELCC and PLR will be re-calculated during the annual VOS adjustment and thus reflect any
increase in future PV Penetration Levels.
The ELCC and PLR values are used in the Example in Figure 3, VOS Levelized Calculation Chart (p.42)
Effective Load Carrying Capability (ELCC) (p.18)
The Effective Load Carrying Capability (ELCC) is the measure of the effective capacity for distributed PV
that can be applied to the avoided generation capacity costs, the avoided reserve capacity costs, the
avoided generation fixed O&M costs, and the avoided transmission capacity costs (see Figure 1).
Using current MISO rules for non-wind variable generation (MISO BPM-011, Section 4.2.2.4, page 35):
the ELCC will be calculated from the PV Fleet Shape for hours ending 2pm, 3pm, and 4pm Central
Standard Time during June, July, and August over the most recent three years. If three years of data are
unavailable, MISO requires “a minimum of 30 consecutive days of historical data during June, July, or
August” for the hours ending 2pm, 3pm and 4pm Central Standard Time.
The ELCC is calculated by averaging the PV Fleet Shape over the specified hours, and then dividing by the
rating of the Marginal PV Resource (1 kW-AC), which results in a percentage value. Additionally, the
ELCC must be calculated for the two loss cases (with and without T&D losses, as described in the Loss
Analysis subsection).
Peak Load Reduction (PLR)(p.18)
The PLR is defined as the maximum distribution load over the Load Analysis Period (without the
Marginal PV Resource) minus the maximum distribution load over the Load Analysis Period (with the
Marginal PV Resource). The distribution load is the power entering the distribution system from the
transmission system (i.e., generation load minus transmission losses). In calculating the PLR, it is not
sufficient to limit modeling to the peak hour. All hours over the Load Analysis Period must be included in
the calculation. This is because the reduced peak load may not occur in the same hour as the original
peak load.
The PLR is calculated as follows. First, determine the maximum Hourly Distribution Load (D1) over the
Load Analysis Period. Next, create a second hourly distribution load time series by subtracting the effect
of the Marginal PV Resource, i.e., by evaluating what the new distribution load would be each hour
given the PV Fleet Shape. Next, determine the maximum load in the second time series (D2). Finally,
calculate the PLR by subtracting D2 from D1.
In other words, the PLR represents the capability of the Marginal PV Resource to reduce the peak
distribution load over the Load Analysis Period. PLR is expressed in kW per kW-AC.
Additionally, the PLR must be calculated for the two loss cases (with distribution losses and without
distribution losses, as described in the Loss Analysis subsection).
Loss Savings Analysis (p.19)
Losses to be considered are described in Table 7
Loss Savings Factors
The Energy Loss Savings Factor (as a percentage) is defined for use within the VOS Calculation Table:
Equation 4 (p.20)
[Annual Avoided Energy (with losses) ] = | [Annual avoided Energy (without losses)] *[1 + Loss Savings (Energy)
Equation 5 (equation rearranged) (p.20)
Loss Savings (energy) = | [[Annual Avoided Energy (with losses)] / [Annual avoided Energy (without losses)]] - 1
In the example this equation produces the 8% of PV Output.
The Loss saving factor for energy of 8% is used in Figure 3, VOS Levelized Calculation Chart (p. 42)
the PLR Loss Savings Factor is defined as:
Equation 6 (p. 20)
Loss Savings (PLR) = | [[PLR (with losses)] / [PLR (without losses)]] - 1
In the example this equation produces the 5% of PV Output.
The Loss saving factor for PLR of 5% is used in Figure 3, VOS Levelized Calculation Chart (p. 42)
the ELCC Loss Savings Factor is defined as:
Equation 7 (p.20)
Loss Savings (ELCC) = | [[ELCC (with losses)] / [ELCC (without losses)]] - 1
In the example this equation produces the 9% of PV Output.
The Loss saving factor for ELCC of 9% is used in Figure 3, VOS Levelized Calculation Chart (p. 42)
PV Energy (p. 14-17)
PV System Rating Conversion: Rating (kW-AC) = [Module Quantity] * [Module PTC rating (kW)] * [Inverter Efficiency Rating] * [Loss Factor]
pg 14. The methodology uses a rating convention for PV capacity based on AC delivered energy (not DC), taking
into account losses internal to the PV system. A PV system rated output is calculated by multiplying the
number of modules by the module PTC rating [as listed by the California Energy Commission (CEC)] to
account for module de-rate effects. The result is then multiplied by the CEC-listed inverter efficiency
rating to account for inverter efficiency, and the result is multiplied by a loss factor to account for
internal PV array losses (wiring losses, module mismatch and other losses).
If no CEC module PTC rating is available, the module PTC rating should be calculated as 0.90 times the
module STC rating8. If no CEC inverter efficiency rating is available, an inverter efficiency of 0.95 should
be used. If no measured or design loss factor is available, 0.85 should be used.
Hourly Fleet Production: Three methods described on pages 14-16
PV Fleet Shape: pg 17.
Regardless of which of the three methods is selected for obtaining the Hourly PV Fleet production, the
next step is divide each hour’s value by the PV Fleet's aggregate AC rating to obtain the PV Fleet Shape.
The units of the PV Fleet Shape are kWh per hour per kW-AC (or, equivalently, average kW per kW-AC).
Marginal PV Resource
The PV Fleet Shape is hourly production of a Marginal PV Resource having a rating of 1 kW-AC.
Annual Avoided Energy:
Annual Avoided Energy (kWh per kW-AC per year) is the sum of the hourly PV Fleet Shape across all
hours of the Load Analysis Period, divided by the numbers of years in the Load Analysis Period. The
result is the annual output of the Marginal PV Resource.
Equation 3 (p.17)
Annual Avoided Energy (kWh) = | (Sum Hourly PV Fleet Production)/(NumberOfYearsInLoadAnalysisPeriod)
In the example this equation produces the 1800 kWh per kW-AC in Table 5.
The 1800 kWh per kWAC figure is used in Tables 8-13, 15 and 17.
Defined in this way, the Annual Avoided Energy does not include the effects of loss savings. As
described in the Loss Analysis subsection, however, it will have to be calculated for the two loss
cases (with losses and without losses)
Transmission (p.30)
Avoided transmission capacity costs are calculated based on the utility’s 5-year average
MISO OATT Schedule 9 charge in Start Year USD, e.g., in 2014 USD if year one of the VOS tariff was
2014. Table 13 shows the example calculation.
Power Generation (p.28)
The solar-weighted capacity cost is based on the installed capital cost of a peaking combustion turbine
and the installed capital cost of a combined cycle gas turbine, interpolated based on heat rate:
Equation 17 (p. 17)
Cost = | Cost(ccgt) + (HeatRate(pv) - HeatRate(ccgt) * [(Cost(ct) - Cost(ccgt))/(HeatRate(ct) - HeatRate(ccgt))]
Where, from Table 5 above,
|  | Cost (CCGT) | = | 1200
|  | Heat Rate (pv) | = | 8000
|  | Heat Rate (CCGT) | = | 6500
|  | Cost (CT) | = | 900
|  | Heat Rate (CT) | = | 9500
Equation 17 is used for calculating Avoided Generation Capacity Costs in Table 11.
Solar-weighted heat rate (p.23)
For the Futures Market option, Guaranteed NG prices are calculated as follows. Prices for the first 12
years are based on NYMEX futures, with each monthly price averaged to give a 12-month average in $
per MMBtu. Prices for years beyond this NYMEX limit are calculated by applying the assumed annual
NYMEX price escalation. An assumed fuel price overhead amount, escalated by year using the assumed
NYMEX price escalation, is added to the fuel price to give the burnertip fuel price.
The first-year solar-weighted heat rate is calculated as follows:
Equation 14 (p. 23)
| Solar Weighted Heat Rate (0) = |  | (Σheat Rate × Fleet Production (j))/Σ Fleet Production (j)
The 8000 BTU per kWh is used in Table 8 for the first year in column "Heat Rate" and, likewise, also in Table 17
where the summation is over all hours j of the load analysis period, HeatRate is the actual heat rate of
the plant on the margin, and FleetProduction is the Fleet Production Shape time series.
Generation life
Fuel Price Overhead (p. 23)
An assumed fuel price overhead amount, escalated by year using the assumed
NYMEX price escalation, is added to the fuel price to give the burnertip fuel price.
In the example and assumed fuel price overhead of $0.50 was used in Table 8, under the column titled "Fuel Price Overhead."
Heat Rate Degradation Rate (p. 23)
The solar-weighted heat rate for future years is calculated as:
Equation 15 (p. 23)
| Solar Weighted Heat Rate (i) = |  | Solar Weighted Heat Rate (0) × (1 + HeatRateDegradationRate)
O&M cost (first year) - Fixed and Variable (p. 24 - 27)
The first year fixed value is escalated at the O&M escalation rate for future years.
O&M calculations are given in Tables 9 and 10
Reserve planning margin
An example of the calculation of avoided reserve capacity cost is shown in Table 12. This is identical to
the generation capacity cost calculation, except utility costs are multiplied by the reserve capacity
margin. In the example, the reserve capacity margin is 15%, so the utility cost for 2014 is calculated as
$86 per unit effective capacity x 15% = $13. The rest of the calculation is identical to the capacity cost
calculation.
Distribution (p. 35)
Future growth in peak load is assumed to be at the same rate as the last 10 years. It is calculated using
the ratio of peak loads of the most recent year (year 10) and the peak load from the earlier year (year 1):
Equation 18 (p. 35)
| GrowthRate = | [(P(10)/P(1))^0.1)] - 1
A sample economic value calculation is presented in Table 15. The distribution cost for the first year
($200 per kW in the example) is taken from the analysis of historical cost and growth as described
above. This cost is escalated each year using the rate in the VOS Data Table.
Table 5 values for Capacity-related distribution capital cost, Distribution capital cost escalation, Peak Load, and Peak Load Growth Rate
are used in Tables 15. They are used to estimate capacity-related distribution capital costs over the next 25 years. For example,
peak load is 5000 MW, so the new capacity in the first year is 1% of this, or 50 MW. At $200 per kW, this is $10M. This is carried on for the remaining 25 years.
The growth rate of the peak load is calculated using equation 18.

## Table 6
Table 6. (EXAMPLE) Azimuth and tilt angles.
System | Azimuth | Tilt | % capacity
1 | 90 | 20 | 3.5
2 | 135 | 15 | 3
3 | 135 | 30 | 6.5
4 | 180 | 0 | 6
5 | 180 | 15 | 16
6 | 180 | 25 | 22.5
7 | 180 | 35 | 18
8 | 235 | 15 | 8.5
9 | 235 | 30 | 9
10 | 270 | 20 | 7
11
12
13
14
15
** (Example) Azimuth and tilt angles
For Method 3 for determining Hourly PV Fleet Production when neither metered production data nor detailed PV system specification are available.
Expected Fleet, Simulated Production. If neither metered production data nor detailed PV
system specifications are available, a diverse set of PV resources can be estimated by simulating
groups of systems at major load centers in the utility's service territory with some assumed fleet
configuration. To use this method, one or more of the largest load centers in the utility service
territory may be used. If a single load center accounts for a high percentage of the utility's total
load, a single location will suffice. If there are several large load centers in the territory, groups
of systems can be created at each location with capacities proportional to the load in that area.
For each location, simulate multiple systems, each rated in proportion to the expected
capacity, with azimuth and tilt angles such as the list of systems presented in Table 6.

## Table 8
|  |  | 3.93* (1+0.047737)^Year |  |  |  | Prices |  |  | Costs |  |  | Disc. Costs
Year | Analysis Period | Guaranteed NG Price | Guaranteed NG Price | Fuel Price Overhead | Burnertip NG Price | Heat Rate | Uitility | VOS | p.u. PV Production | Utility | VOS | Discount Factor (risk free) | Utility | VOS
|  | ($/MMBtu) | ($/MMBtu) | ($) | ($/MMBtu) | (Btu/kWh) | ($/kWh) | ($/kWh) | (kWh) | ($) | ($) |  | ($) | ($)
2014 | 0 | 4.5025 | 4.5025 | -0.04 | 4.4625 | 6950.164 | 0.031015 | 0.03689 | 1451.6947 | 45.0249 | 53.5524 | 1 | 45.0249 | 53.5524
2015 | 1 | 4.258 | 4.6264 | -0.0411 | 4.2169 | 6957.1142 | 0.029337 | 0.03689 | 1444.4362 | 42.3758 | 53.2847 | 0.9987 | 42.3208 | 53.2155
2016 | 2 | 4.1986 | 4.7536 | -0.04223 | 4.1564 | 6964.0713 | 0.028946 | 0.03689 | 1437.214 | 41.601 | 53.0183 | 0.99423 | 41.3607 | 52.7121
2017 | 3 | 4.2727 | 4.8843 | -0.043392 | 4.2293 | 6971.0354 | 0.029483 | 0.03689 | 1430.0279 | 42.1613 | 52.7532 | 0.98574 | 41.56 | 52.0008
2018 | 4 | 4.3692 | 5.0186 | -0.044585 | 4.3246 | 6978.0064 | 0.030177 | 0.03689 | 1422.8778 | 42.9383 | 52.4894 | 0.97075 | 41.6822 | 50.9539
2019 | 5 | 4.4936 | 5.1566 | -0.045811 | 4.4478 | 6984.9844 | 0.031068 | 0.03689 | 1415.7634 | 43.9843 | 52.227 | 0.95099 | 41.8288 | 49.6676
2020 | 6 | 4.6893 | 5.2984 | -0.047071 | 4.6422 | 6991.9694 | 0.032458 | 0.03689 | 1408.6846 | 45.7236 | 51.9658 | 0.92708 | 42.3893 | 48.1762
2021 | 7 | 4.859 | 5.4442 | -0.048365 | 4.8107 | 6998.9614 | 0.03367 | 0.03689 | 1401.6412 | 47.1928 | 51.706 | 0.89916 | 42.4341 | 46.4922
2022 | 8 | 5.0028 | 5.5939 | -0.049695 | 4.9531 | 7005.9603 | 0.034701 | 0.03689 | 1394.633 | 48.3956 | 51.4475 | 0.87155 | 42.1794 | 44.8392
2023 | 9 | 5.0913 | 5.7477 | -0.051062 | 5.0402 | 7012.9663 | 0.035347 | 0.03689 | 1387.6598 | 49.0496 | 51.1902 | 0.84145 | 41.2725 | 43.0738
2024 | 10 | 5.1458 | 5.9058 | -0.052466 | 5.0934 | 7019.9793 | 0.035755 | 0.03689 | 1380.7215 | 49.3682 | 50.9343 | 0.80917 | 39.9474 | 41.2146
2025 | 11 | 5.2398 | 6.0682 | -0.053909 | 5.1859 | 7026.9992 | 0.036441 | 0.03689 | 1373.8179 | 50.064 | 50.6796 | 0.7856 | 39.33 | 39.8137
2026 | 12 | 5.3839 | 6.235 | -0.055391 | 5.3285 | 7034.0262 | 0.037481 | 0.03689 | 1366.9488 | 51.2347 | 50.4262 | 0.76155 | 39.0176 | 38.4019
2027 | 13 | 5.532 | 6.4065 | -0.056915 | 5.4751 | 7041.0603 | 0.03855 | 0.03689 | 1360.1141 | 52.4328 | 50.1741 | 0.73711 | 38.6489 | 36.984
2028 | 14 | 5.6841 | 6.5827 | -0.05848 | 5.6256 | 7048.1013 | 0.03965 | 0.03689 | 1353.3135 | 53.659 | 49.9232 | 0.71238 | 38.2258 | 35.5645
2029 | 15 | 5.8404 | 6.7637 | -0.060088 | 5.7803 | 7055.1494 | 0.040781 | 0.03689 | 1346.5469 | 54.9138 | 49.6736 | 0.68744 | 37.75 | 34.1477
2030 | 16 | 6.001 | 6.9497 | -0.06174 | 5.9393 | 7062.2046 | 0.041945 | 0.03689 | 1339.8142 | 56.1979 | 49.4252 | 0.66237 | 37.2238 | 32.7378
2031 | 17 | 6.1661 | 7.1408 | -0.063438 | 6.1026 | 7069.2668 | 0.043141 | 0.03689 | 1333.1151 | 57.5121 | 49.1781 | 0.63725 | 36.6495 | 31.3387
2032 | 18 | 6.3356 | 7.3372 | -0.065183 | 6.2705 | 7076.336 | 0.044372 | 0.03689 | 1326.4496 | 58.857 | 48.9322 | 0.61216 | 36.0297 | 29.9541
2033 | 19 | 6.5099 | 7.539 | -0.066975 | 6.4429 | 7083.4124 | 0.045638 | 0.03689 | 1319.8173 | 60.2334 | 48.6875 | 0.58717 | 35.3669 | 28.5876
2034 | 20 | 6.6889 | 7.7463 | -0.068817 | 6.6201 | 7090.4958 | 0.04694 | 0.03689 | 1313.2182 | 61.6419 | 48.4441 | 0.56235 | 34.6642 | 27.2424
2035 | 21 | 6.8728 | 7.9593 | -0.07071 | 6.8021 | 7097.5863 | 0.048279 | 0.03689 | 1306.6521 | 63.0834 | 48.2019 | 0.5425 | 34.2231 | 26.1498
2036 | 22 | 7.0618 | 8.1782 | -0.072654 | 6.9892 | 7104.6839 | 0.049656 | 0.03689 | 1300.1189 | 64.5586 | 47.9609 | 0.52301 | 33.7647 | 25.0839
2037 | 23 | 7.256 | 8.4031 | -0.074652 | 7.1814 | 7111.7886 | 0.051072 | 0.03689 | 1293.6183 | 66.0683 | 47.7211 | 0.50387 | 33.2899 | 24.0453
2038 | 24 | 7.4556 | 8.6342 | -0.076705 | 7.3789 | 7118.9003 | 0.052529 | 0.03689 | 1287.1502 | 67.6133 | 47.4825 | 0.48511 | 32.7996 | 23.034
*Avoided Fuel Cost
**Economic Value of Avoided Fuel Costs | [10 empty] | Validation: Present Value |  | 968.9836 | 968.9836
[9 empty] | Levelized Cost |  | 0.03689
pg.22 - 24:
Avoided fuel costs are based on long-term, risk-free fuel supply contracts. This value implicitly includes
both the avoided cost of fuel as well as the avoided cost of price volatility risk that is otherwise passed
from the utility to customers through fuel price adjustments.
PV displaces energy generated from the marginal unit, so it avoids the cost of fuel associated with this | [10 empty] | 130
generation. Furthermore, the PV system is assumed to have a service life of 25 years, so the uncertainty | [10 empty] | 0.018705
in fuel price fluctuations is also eliminated over this period. For this reason, the avoided fuel cost must
take into account the fuel as if it were purchased under a guaranteed, long term contract.
The methodology provides for three options to accomplish this:
| Futures Market. |  |  | This option is described in detail below, and is based on the NYMEX NG futures
with a fixed escalation for years beyond the 12-year trading period.
| Long Term Price Quotation. |  |  | This option is identical to the above option, except the input pricing
data is based on an actual price quotation from an AA-rated NG supplier to lock in prices for the
25-year guaranteed period.
| Utility-guaranteed Price. |  |  | This is the 25-year fuel price that is guaranteed by the utilities. Tariffs
using the utility guaranteed price will include a mechanism for removing the usage fuel
adjustment charges and provide fixed prices over the term.
For the Futures Market option, Guaranteed NG prices are calculated as follows. Prices for the first 12
years are based on NYMEX futures, with each monthly price averaged to give a 12-month average in $
per MMBtu. Prices for years beyond this NYMEX limit are calculated by applying the assumed annual
NYMEX price escalation. An assumed fuel price overhead amount, escalated by year using the assumed
NYMEX price escalation, is added to the fuel price to give the burnertip fuel price.
The utility price in year i is:
Equation 16 (p.23)
| UtilityPrice (i) = |  | (BurnertipFuelPrice(i) × SolarWeightedHeatRate)/10^6
Equation 16 is used for Column H above, Utility Price. It is divided by 10^6 to convert Mmbtu to btus.
where the burnertip price is in $ per MMBtu and the heat rate is in Btu per kWh.
Utility cost is the product of the utility price and the per unit PV production. These costs are then
discounted using the risk free discount rate and summed for all years. A risk-free discount rate (fitted to
the US Treasury yields shown in Table 3) has been selected to account for the fact that there is no risk in
the avoided fuel cost.
The VOS price (shown in red in Table 8) is the levelized amount that results in the same discounted
amount as the utility price for the Avoided Fuel Cost component.

## Table 9
[6 empty] | Costs |  |  | Disc. Costs |  | Prices
Year | Analysis Period | O&M Fixed | Utility Capacity | PV Capacity | p.u PV Production | Utility | VOS | Discount Factor | Utility | VOS | Utility | VOS
|  | ($/kW) | (p.u.) | (kW) | (kWh) | ($) | ($) |  | ($) | ($) | ($/kWh) | ($/kWh)
2014 | 0 | 2.0045 | 1 | 1 | 1451.6947 | 2.0045 | 2.3468 | 1 | 2.0045 | 2.3468 | 0.0013808 | 0.0016166 | 0.0013808
2015 | 1 | 2.0378 | 0.999 | 0.995 | 1444.4362 | 2.0296 | 2.3351 | 0.93888 | 1.9056 | 2.1923 | 0.0014108 | 0.0016166
2016 | 2 | 2.0716 | 0.998 | 0.99003 | 1437.214 | 2.055 | 2.3234 | 0.88149 | 1.8115 | 2.048 | 0.0014414 | 0.0016166
2017 | 3 | 2.106 | 0.997 | 0.98507 | 1430.0279 | 2.0808 | 2.3118 | 0.82762 | 1.7221 | 1.9133 | 0.0014727 | 0.0016166
2018 | 4 | 2.1409 | 0.99601 | 0.98015 | 1422.8778 | 2.1069 | 2.3002 | 0.77703 | 1.6371 | 1.7873 | 0.0015047 | 0.0016166
2019 | 5 | 2.1765 | 0.99501 | 0.97525 | 1415.7634 | 2.1333 | 2.2887 | 0.72954 | 1.5563 | 1.6697 | 0.0015373 | 0.0016166
2020 | 6 | 2.2126 | 0.99401 | 0.97037 | 1408.6846 | 2.16 | 2.2773 | 0.68495 | 1.4795 | 1.5598 | 0.0015707 | 0.0016166
2021 | 7 | 2.2493 | 0.99302 | 0.96552 | 1401.6412 | 2.187 | 2.2659 | 0.64308 | 1.4065 | 1.4571 | 0.0016048 | 0.0016166
2022 | 8 | 2.2867 | 0.99203 | 0.96069 | 1394.633 | 2.2144 | 2.2545 | 0.60378 | 1.337 | 1.3612 | 0.0016396 | 0.0016166
2023 | 9 | 2.3246 | 0.99104 | 0.95589 | 1387.6598 | 2.2422 | 2.2433 | 0.56687 | 1.271 | 1.2717 | 0.0016752 | 0.0016166
2024 | 10 | 2.3632 | 0.99004 | 0.95111 | 1380.7215 | 2.2703 | 2.2321 | 0.53223 | 1.2083 | 1.188 | 0.0017116 | 0.0016166
2025 | 11 | 2.4025 | 0.98905 | 0.94635 | 1373.8179 | 2.2987 | 2.2209 | 0.4997 | 1.1487 | 1.1098 | 0.0017487 | 0.0016166
2026 | 12 | 2.4423 | 0.98807 | 0.94162 | 1366.9488 | 2.3275 | 2.2098 | 0.46915 | 1.092 | 1.0367 | 0.0017867 | 0.0016166
2027 | 13 | 2.4829 | 0.98708 | 0.93691 | 1360.1141 | 2.3567 | 2.1987 | 0.44048 | 1.0381 | 0.9685 | 0.0018255 | 0.0016166
2028 | 14 | 2.5241 | 0.98609 | 0.93223 | 1353.3135 | 2.3862 | 2.1877 | 0.41356 | 0.98684 | 0.90476 | 0.0018651 | 0.0016166
2029 | 15 | 2.566 | 0.9851 | 0.92757 | 1346.5469 | 2.4161 | 2.1768 | 0.38828 | 0.93813 | 0.84521 | 0.0019056 | 0.0016166
2030 | 16 | 2.6086 | 0.98412 | 0.92293 | 1339.8142 | 2.4464 | 2.1659 | 0.36455 | 0.89183 | 0.78958 | 0.001947 | 0.0016166
2031 | 17 | 2.6519 | 0.98314 | 0.91832 | 1333.1151 | 2.477 | 2.1551 | 0.34227 | 0.84781 | 0.73762 | 0.0019892 | 0.0016166
2032 | 18 | 2.6959 | 0.98215 | 0.91372 | 1326.4496 | 2.5081 | 2.1443 | 0.32135 | 0.80596 | 0.68907 | 0.0020324 | 0.0016166
2033 | 19 | 2.7407 | 0.98117 | 0.90916 | 1319.8173 | 2.5395 | 2.1336 | 0.30171 | 0.76618 | 0.64372 | 0.0020765 | 0.0016166
2034 | 20 | 2.7862 | 0.98019 | 0.90461 | 1313.2182 | 2.5713 | 2.1229 | 0.28326 | 0.72837 | 0.60135 | 0.0021216 | 0.0016166
2035 | 21 | 2.8324 | 0.97921 | 0.90009 | 1306.6521 | 2.6035 | 2.1123 | 0.26595 | 0.69242 | 0.56177 | 0.0021677 | 0.0016166
2036 | 22 | 2.8794 | 0.97823 | 0.89559 | 1300.1189 | 2.6362 | 2.1018 | 0.2497 | 0.65824 | 0.5248 | 0.0022147 | 0.0016166
2037 | 23 | 2.9272 | 0.97725 | 0.89111 | 1293.6183 | 2.6692 | 2.0912 | 0.23443 | 0.62575 | 0.49026 | 0.0022628 | 0.0016166
2038 | 24 | 2.9858 | 0.97627 | 0.88665 | 1287.1502 | 2.7117 | 2.0808 | 0.22011 | 0.59686 | 0.45799 | 0.0023197 | 0.0016166
[7 empty] | Validation: Present Value |  | 29.1564 | 29.1564
[5 empty] | Levelized Cost |  | 0.0016166
** Avoided Plant O&M - Fixed
*** (Example) Economic value of avoided plant O&M - fixed | [5 empty] | Levelized
page 24:
Economic value calculations for fixed plant O&M are presented in Table 9. The first year fixed value is
escalated at the O&M escalation rate for future years.
Similarly, PV capacity has an initial value of one during the first year because it is applicable to PV
systems installed in the first year. Note that effective capacity (load matching) is handled separately, and
this table represents the “ideal” resource, as if PV were able to receive the same capacity credit as a
fully dispatchable technology.
Fixed O&M is avoided only when the resource requiring fixed O&M is avoided. For example, if new
generation is not needed for two years, then the associated fixed O&M is also not needed for two years.
In the example calculation, generation is assumed to be needed for all years, so the avoided cost is
calculated for all years.
The utility cost is the fixed O&M cost times the PV capacity divided by the utility capacity. Utility prices
are the cost divided by the PV production. Costs are discounted using the utility discount factor and are
summed for all years.
The VOS component value is calculated as before such that the discounted total is equal to the
discounted utility cost.

## Table 10
Table 10. (Example) Economic value of avoided plant O&M - Variable
|  | Prices |  |  | Costs |  |  | Disc. Costs
Year | Analysis Period | Utility | VOS | p.u. PV Production | Utility | VOS | Discount Factor | Utility | VOS
|  | ($/kWh) | ($/kWh) | (kWh) | ($) | ($) |  | ($) | ($)
2014 | 0 | 0.0013539 | 0.0015702 | 1451.6947 | 1.9655 | 2.2794 | 1 | 1.9655 | 2.2794
2015 | 1 | 0.0013764 | 0.0015702 | 1444.4362 | 1.9881 | 2.268 | 0.93888 | 1.8666 | 2.1294
2016 | 2 | 0.0013993 | 0.0015702 | 1437.214 | 2.011 | 2.2567 | 0.88149 | 1.7727 | 1.9893
2017 | 3 | 0.0014225 | 0.0015702 | 1430.0279 | 2.0342 | 2.2454 | 0.82762 | 1.6835 | 1.8583
2018 | 4 | 0.0014461 | 0.0015702 | 1422.8778 | 2.0576 | 2.2342 | 0.77703 | 1.5988 | 1.736
2019 | 5 | 0.0014701 | 0.0015702 | 1415.7634 | 2.0813 | 2.223 | 0.72954 | 1.5184 | 1.6218
2020 | 6 | 0.0014945 | 0.0015702 | 1408.6846 | 2.1053 | 2.2119 | 0.68495 | 1.442 | 1.515
2021 | 7 | 0.0015193 | 0.0015702 | 1401.6412 | 2.1295 | 2.2008 | 0.64308 | 1.3695 | 1.4153
2022 | 8 | 0.0015445 | 0.0015702 | 1394.633 | 2.1541 | 2.1898 | 0.60378 | 1.3006 | 1.3222
2023 | 9 | 0.0015702 | 0.0015702 | 1387.6598 | 2.1789 | 2.1789 | 0.56687 | 1.2352 | 1.2352
2024 | 10 | 0.0015962 | 0.0015702 | 1380.7215 | 2.204 | 2.168 | 0.53223 | 1.173 | 1.1539
2025 | 11 | 0.0016227 | 0.0015702 | 1373.8179 | 2.2294 | 2.1572 | 0.4997 | 1.114 | 1.0779
2026 | 12 | 0.0016497 | 0.0015702 | 1366.9488 | 2.255 | 2.1464 | 0.46915 | 1.058 | 1.007
2027 | 13 | 0.0016771 | 0.0015702 | 1360.1141 | 2.281 | 2.1356 | 0.44048 | 1.0047 | 0.9407
2028 | 14 | 0.0017049 | 0.0015702 | 1353.3135 | 2.3073 | 2.125 | 0.41356 | 0.95419 | 0.87879
2029 | 15 | 0.0017332 | 0.0015702 | 1346.5469 | 2.3338 | 2.1143 | 0.38828 | 0.90618 | 0.82095
2030 | 16 | 0.001762 | 0.0015702 | 1339.8142 | 2.3607 | 2.1038 | 0.36455 | 0.8606 | 0.76692
2031 | 17 | 0.0017912 | 0.0015702 | 1333.1151 | 2.3879 | 2.0932 | 0.34227 | 0.8173 | 0.71644
2032 | 18 | 0.001821 | 0.0015702 | 1326.4496 | 2.4154 | 2.0828 | 0.32135 | 0.77618 | 0.66929
2033 | 19 | 0.0018512 | 0.0015702 | 1319.8173 | 2.4432 | 2.0724 | 0.30171 | 0.73714 | 0.62524
2034 | 20 | 0.0018819 | 0.0015702 | 1313.2182 | 2.4714 | 2.062 | 0.28326 | 0.70005 | 0.58409
2035 | 21 | 0.0019132 | 0.0015702 | 1306.6521 | 2.4998 | 2.0517 | 0.26595 | 0.66483 | 0.54565
2036 | 22 | 0.0019449 | 0.0015702 | 1300.1189 | 2.5286 | 2.0414 | 0.2497 | 0.63139 | 0.50974
2037 | 23 | 0.0019772 | 0.0015702 | 1293.6183 | 2.5577 | 2.0312 | 0.23443 | 0.59962 | 0.47619
2038 | 24 | 0.00201 | 0.0015702 | 1287.1502 | 2.5872 | 2.0211 | 0.22011 | 0.56946 | 0.44485
[5 empty] | Validation: Present Value |  |  | 28.3195 | 28.3195
|  | Levelized Cost of Solar |  | 0.0015702
** Avoided Plant O&M Variable
*** (Example) Economic value of avoided plant O&M - variable
pg. 27:
An example calculation of avoided plant O&M is displayed in Table 10. Utility prices are given in the VOS
Data Table, escalated each year by the O&M escalation rate. As before, the per unit PV production is
shown with annual degradation taken into account. The utility cost is the product of the utility price and
the per unit production, and these costs are discounted. The VOS price of variable O&M is the levelized
value resulting in the same total discounted cost.

## Table 11
Table 11. (EXAMPLE) Economic value of avoided generation capacity cost
[6 empty] | Costs |  |  | Disc. Costs |  | Prices
Year | Analysis Period | Capacity Cost | Utility Capacity | PV Capacity | p.u. PV Production | Utility | VOS | Discount Factor | Utility | VOS | Utility | VOS
|  | ($/kW-yr) | (p.u.) | (kW) | (kWh) | ($) | ($) |  | ($) | ($) | ($/kWh) | ($/kWh)
2014 | 0 | 63.4985 | 1 | 1 | 1451.6947 | 63.4985 | 64.05 | 1 | 63.4985 | 64.05 | 0.043741 | 0.044121
2015 | 1 | 63.4985 | 0.999 | 0.995 | 1444.4362 | 63.2443 | 63.7297 | 0.93888 | 59.3787 | 59.8345 | 0.043785 | 0.044121
2016 | 2 | 63.4985 | 0.998 | 0.99003 | 1437.214 | 62.991 | 63.4111 | 0.88149 | 55.5262 | 55.8964 | 0.043829 | 0.044121
2017 | 3 | 63.4985 | 0.997 | 0.98507 | 1430.0279 | 62.7388 | 63.094 | 0.82762 | 51.9236 | 52.2176 | 0.043872 | 0.044121
2018 | 4 | 63.4985 | 0.99601 | 0.98015 | 1422.8778 | 62.4876 | 62.7785 | 0.77703 | 48.5548 | 48.7809 | 0.043916 | 0.044121
2019 | 5 | 63.4985 | 0.99501 | 0.97525 | 1415.7634 | 62.2374 | 62.4646 | 0.72954 | 45.4046 | 45.5703 | 0.04396 | 0.044121
2020 | 6 | 63.4985 | 0.99401 | 0.97037 | 1408.6846 | 61.9882 | 62.1523 | 0.68495 | 42.4587 | 42.5711 | 0.044004 | 0.044121
2021 | 7 | 63.4985 | 0.99302 | 0.96552 | 1401.6412 | 61.74 | 61.8416 | 0.64308 | 39.704 | 39.7693 | 0.044048 | 0.044121
2022 | 8 | 63.4985 | 0.99203 | 0.96069 | 1394.633 | 61.4928 | 61.5323 | 0.60378 | 37.128 | 37.1518 | 0.044092 | 0.044121
2023 | 9 | 63.4985 | 0.99104 | 0.95589 | 1387.6598 | 61.2466 | 61.2247 | 0.56687 | 34.7191 | 34.7067 | 0.044137 | 0.044121
2024 | 10 | 63.4985 | 0.99004 | 0.95111 | 1380.7215 | 61.0013 | 60.9186 | 0.53223 | 32.4665 | 32.4224 | 0.044181 | 0.044121
2025 | 11 | 63.4985 | 0.98905 | 0.94635 | 1373.8179 | 60.7571 | 60.614 | 0.4997 | 30.3601 | 30.2885 | 0.044225 | 0.044121
2026 | 12 | 63.4985 | 0.98807 | 0.94162 | 1366.9488 | 60.5138 | 60.3109 | 0.46915 | 28.3903 | 28.2951 | 0.044269 | 0.044121
2027 | 13 | 63.4985 | 0.98708 | 0.93691 | 1360.1141 | 60.2715 | 60.0093 | 0.44048 | 26.5483 | 26.4328 | 0.044314 | 0.044121
2028 | 14 | 63.4985 | 0.98609 | 0.93223 | 1353.3135 | 60.0302 | 59.7093 | 0.41356 | 24.8259 | 24.6932 | 0.044358 | 0.044121
2029 | 15 | 63.4985 | 0.9851 | 0.92757 | 1346.5469 | 59.7898 | 59.4107 | 0.38828 | 23.2152 | 23.068 | 0.044402 | 0.044121
2030 | 16 | 63.4985 | 0.98412 | 0.92293 | 1339.8142 | 59.5504 | 59.1137 | 0.36455 | 21.7089 | 21.5497 | 0.044447 | 0.044121
2031 | 17 | 63.4985 | 0.98314 | 0.91832 | 1333.1151 | 59.312 | 58.8181 | 0.34227 | 20.3005 | 20.1314 | 0.044491 | 0.044121
2032 | 18 | 63.4985 | 0.98215 | 0.91372 | 1326.4496 | 59.0745 | 58.524 | 0.32135 | 18.9834 | 18.8065 | 0.044536 | 0.044121
2033 | 19 | 63.4985 | 0.98117 | 0.90916 | 1319.8173 | 58.838 | 58.2314 | 0.30171 | 17.7517 | 17.5687 | 0.04458 | 0.044121
2034 | 20 | 63.4985 | 0.98019 | 0.90461 | 1313.2182 | 58.6024 | 57.9403 | 0.28326 | 16.6 | 16.4124 | 0.044625 | 0.044121
2035 | 21 | 63.4985 | 0.97921 | 0.90009 | 1306.6521 | 58.3677 | 57.6506 | 0.26595 | 15.523 | 15.3322 | 0.04467 | 0.044121
2036 | 22 | 63.4985 | 0.97823 | 0.89559 | 1300.1189 | 58.134 | 57.3623 | 0.2497 | 14.5158 | 14.3231 | 0.044714 | 0.044121
2037 | 23 | 63.4985 | 0.97725 | 0.89111 | 1293.6183 | 57.9013 | 57.0755 | 0.23443 | 13.574 | 13.3805 | 0.044759 | 0.044121
2038 | 24 | 63.4985 | 0.97627 | 0.88665 | 1287.1502 | 57.6694 | 56.7901 | 0.22011 | 12.6934 | 12.4998 | 0.044804 | 0.044121
[11 empty] | 0.47079 | NPV
[11 empty] | 0.044103 | PMT
[6 empty] | Validation: Present Value |  |  | 795.7531 | 795.7531
[6 empty] | Levelized Costs |  | 0.044121
** Avoided Generation Capacity Cost
Table 5
The solar-weighted capacity cost is based on the installed capital cost of a peaking combustion turbine | [12 empty] | Cost (CCGT) |  | 882
and the installed capital cost of a combined cycle gas turbine, interpolated based on heat rate: | [12 empty] | Heat Rate (pv) |  | 6950.164
[13 empty] | Heat Rate (CCGT) |  | 6777
[13 empty] | Cost (CT) |  | 640
[13 empty] | Heat Rate (CT) |  | 9796
[13 empty] | Cost | 868.1193
Equation 17
| Cost = | Cost(ccgt) + (HeatRate(pv) - HeatRate(ccgt) * [(Cost(ct) - Cost(ccgt))/(HeatRate(ct) - HeatRate(ccgt))] | [9 empty] | Amortized | = | 63.4985
Using equation ( 17 ) with the CT/CCGT heat rates and costs from the example VOS Data Table, we
calculated a solar-weighted capacity cost of $1,050 per kW. In the example, the amortized cost is $86
per kW-yr.
Table 11 illustrates how utility costs are calculated by taking into account the degrading heat rate of the
marginal unit and PV. For example, in year 2015, the utility cost is $86 per kW-yr x 0.999 / 0.995 to give
$85 for each unit of effective PV capacity. Utility prices are back-calculated for reference from the per
unit PV production. Again, the VOS price is selected to give the same total discounted cost as the utility
costs for the Generation Capacity Cost component.

## Table 12
Table 12. (EXAMPLE) Economic Value of avoided reserve capacity cost
[6 empty] | Costs |  |  | Disc. Costs |  | Prices
Year | Analysis Period | Capacity Cost | Gen Capacity | PV Capacity | p.u. PV Production | Utility | VOS | Discount Factor | Utiilty | VOS | Utility | VOS
|  | ($/kW-yr) | (p.u.) | (kW) | (kWh) | ($) | ($) |  | ($) | ($) | ($/kWh) | ($/kWH)
2014 | 0 | 63.4985 | 1 | 1 | 1451.6947 | 4.6354 | 4.6756 | 1 | 4.6354 | 4.6756 | 0.0031931 | 0.0032208
2015 | 1 | 63.4985 | 0.999 | 0.995 | 1444.4362 | 4.6168 | 4.6523 | 0.93888 | 4.3346 | 4.3679 | 0.0031963 | 0.0032208
2016 | 2 | 63.4985 | 0.998 | 0.99003 | 1437.214 | 4.5983 | 4.629 | 0.88149 | 4.0534 | 4.0804 | 0.0031995 | 0.0032208
2017 | 3 | 63.4985 | 0.997 | 0.98507 | 1430.0279 | 4.5799 | 4.6059 | 0.82762 | 3.7904 | 3.8119 | 0.0032027 | 0.0032208
2018 | 4 | 63.4985 | 0.99601 | 0.98015 | 1422.8778 | 4.5616 | 4.5828 | 0.77703 | 3.5445 | 3.561 | 0.0032059 | 0.0032208
2019 | 5 | 63.4985 | 0.99501 | 0.97525 | 1415.7634 | 4.5433 | 4.5599 | 0.72954 | 3.3145 | 3.3266 | 0.0032091 | 0.0032208
2020 | 6 | 63.4985 | 0.99401 | 0.97037 | 1408.6846 | 4.5251 | 4.5371 | 0.68495 | 3.0995 | 3.1077 | 0.0032123 | 0.0032208
2021 | 7 | 63.4985 | 0.99302 | 0.96552 | 1401.6412 | 4.507 | 4.5144 | 0.64308 | 2.8984 | 2.9032 | 0.0032155 | 0.0032208
2022 | 8 | 63.4985 | 0.99203 | 0.96069 | 1394.633 | 4.489 | 4.4919 | 0.60378 | 2.7103 | 2.7121 | 0.0032187 | 0.0032208
2023 | 9 | 63.4985 | 0.99104 | 0.95589 | 1387.6598 | 4.471 | 4.4694 | 0.56687 | 2.5345 | 2.5336 | 0.003222 | 0.0032208
2024 | 10 | 63.4985 | 0.99004 | 0.95111 | 1380.7215 | 4.4531 | 4.4471 | 0.53223 | 2.3701 | 2.3668 | 0.0032252 | 0.0032208
2025 | 11 | 63.4985 | 0.98905 | 0.94635 | 1373.8179 | 4.4353 | 4.4248 | 0.4997 | 2.2163 | 2.2111 | 0.0032284 | 0.0032208
2026 | 12 | 63.4985 | 0.98807 | 0.94162 | 1366.9488 | 4.4175 | 4.4027 | 0.46915 | 2.0725 | 2.0655 | 0.0032317 | 0.0032208
2027 | 13 | 63.4985 | 0.98708 | 0.93691 | 1360.1141 | 4.3998 | 4.3807 | 0.44048 | 1.938 | 1.9296 | 0.0032349 | 0.0032208
2028 | 14 | 63.4985 | 0.98609 | 0.93223 | 1353.3135 | 4.3822 | 4.3588 | 0.41356 | 1.8123 | 1.8026 | 0.0032381 | 0.0032208
2029 | 15 | 63.4985 | 0.9851 | 0.92757 | 1346.5469 | 4.3647 | 4.337 | 0.38828 | 1.6947 | 1.684 | 0.0032414 | 0.0032208
2030 | 16 | 63.4985 | 0.98412 | 0.92293 | 1339.8142 | 4.3472 | 4.3153 | 0.36455 | 1.5848 | 1.5731 | 0.0032446 | 0.0032208
2031 | 17 | 63.4985 | 0.98314 | 0.91832 | 1333.1151 | 4.3298 | 4.2937 | 0.34227 | 1.4819 | 1.4696 | 0.0032479 | 0.0032208
2032 | 18 | 63.4985 | 0.98215 | 0.91372 | 1326.4496 | 4.3124 | 4.2723 | 0.32135 | 1.3858 | 1.3729 | 0.0032511 | 0.0032208
2033 | 19 | 63.4985 | 0.98117 | 0.90916 | 1319.8173 | 4.2952 | 4.2509 | 0.30171 | 1.2959 | 1.2825 | 0.0032544 | 0.0032208
2034 | 20 | 63.4985 | 0.98019 | 0.90461 | 1313.2182 | 4.278 | 4.2296 | 0.28326 | 1.2118 | 1.1981 | 0.0032576 | 0.0032208
2035 | 21 | 63.4985 | 0.97921 | 0.90009 | 1306.6521 | 4.2608 | 4.2085 | 0.26595 | 1.1332 | 1.1193 | 0.0032609 | 0.0032208
2036 | 22 | 63.4985 | 0.97823 | 0.89559 | 1300.1189 | 4.2438 | 4.1874 | 0.2497 | 1.0597 | 1.0456 | 0.0032642 | 0.0032208
2037 | 23 | 63.4985 | 0.97725 | 0.89111 | 1293.6183 | 4.2268 | 4.1665 | 0.23443 | 0.99091 | 0.97677 | 0.0032674 | 0.0032208
2038 | 24 | 63.4985 | 0.97627 | 0.88665 | 1287.1502 | 4.2099 | 4.1457 | 0.22011 | 0.92661 | 0.91249 | 0.0032707 | 0.0032208
[11 empty] | 0.034368 | NPV
[6 empty] | Validation: Present Value |  |  | 58.09 | 58.09 | 0.0032195 | PMT
**Avoided Reserve Capacity Coast
***(Example) Economic value of avoided reserve capacity cost | [7 empty] | Levelized Cost |  | 0.0032208
An example of the calculation of avoided reserve capacity cost is shown in Table 12. This is identical to
the generation capacity cost calculation, except utility costs are multiplied by the reserve capacity
margin. In the example, the reserve capacity margin is 15%, so the utility cost for 2014 is calculated as
$86 per unit effective capacity x 15% = $13. The rest of the calculation is identical to the capacity cost
calculation.

## Table 13
Table 13. (EXAMPLE) Economic value of avoided transmission capacity cost
[6 empty] | Costs |  |  | Disc. Costs |  | Prices
Year | Analysis Period | Capacity Cost | Trans. Capacity | PV Capacity | p.u. PV Production | Utility | VOS | Discount Factor | Utility | VOS | Utility | VOS
|  | ($/kW-yr) | (p.u.) | (kW) | (kWh) | ($) | ($) |  | ($) | ($) | ($) | ($)
2014 | 0 | 40.7161 | 1 | 1 | 1451.6947 | 40.7161 | 40.7161 | 1 | 40.7161 | 40.7161 | 0.028047 | 0.028047
2015 | 1 | 40.7161 | 1 | 0.995 | 1444.4362 | 40.5125 | 40.5125 | 0.93888 | 38.0363 | 38.0363 | 0.028047 | 0.028047
2016 | 2 | 40.7161 | 1 | 0.99003 | 1437.214 | 40.3099 | 40.3099 | 0.88149 | 35.5329 | 35.5329 | 0.028047 | 0.028047
2017 | 3 | 40.7161 | 1 | 0.98507 | 1430.0279 | 40.1084 | 40.1084 | 0.82762 | 33.1943 | 33.1943 | 0.028047 | 0.028047
2018 | 4 | 40.7161 | 1 | 0.98015 | 1422.8778 | 39.9078 | 39.9078 | 0.77703 | 31.0096 | 31.0096 | 0.028047 | 0.028047
2019 | 5 | 40.7161 | 1 | 0.97525 | 1415.7634 | 39.7083 | 39.7083 | 0.72954 | 28.9687 | 28.9687 | 0.028047 | 0.028047
2020 | 6 | 40.7161 | 1 | 0.97037 | 1408.6846 | 39.5097 | 39.5097 | 0.68495 | 27.0621 | 27.0621 | 0.028047 | 0.028047
2021 | 7 | 40.7161 | 1 | 0.96552 | 1401.6412 | 39.3122 | 39.3122 | 0.64308 | 25.281 | 25.281 | 0.028047 | 0.028047
2022 | 8 | 40.7161 | 1 | 0.96069 | 1394.633 | 39.1156 | 39.1156 | 0.60378 | 23.6171 | 23.6171 | 0.028047 | 0.028047
2023 | 9 | 40.7161 | 1 | 0.95589 | 1387.6598 | 38.9201 | 38.9201 | 0.56687 | 22.0628 | 22.0628 | 0.028047 | 0.028047
2024 | 10 | 40.7161 | 1 | 0.95111 | 1380.7215 | 38.7255 | 38.7255 | 0.53223 | 20.6107 | 20.6107 | 0.028047 | 0.028047
2025 | 11 | 40.7161 | 1 | 0.94635 | 1373.8179 | 38.5318 | 38.5318 | 0.4997 | 19.2542 | 19.2542 | 0.028047 | 0.028047
2026 | 12 | 40.7161 | 1 | 0.94162 | 1366.9488 | 38.3392 | 38.3392 | 0.46915 | 17.987 | 17.987 | 0.028047 | 0.028047
2027 | 13 | 40.7161 | 1 | 0.93691 | 1360.1141 | 38.1475 | 38.1475 | 0.44048 | 16.8032 | 16.8032 | 0.028047 | 0.028047
2028 | 14 | 40.7161 | 1 | 0.93223 | 1353.3135 | 37.9567 | 37.9567 | 0.41356 | 15.6972 | 15.6972 | 0.028047 | 0.028047
2029 | 15 | 40.7161 | 1 | 0.92757 | 1346.5469 | 37.767 | 37.767 | 0.38828 | 14.6641 | 14.6641 | 0.028047 | 0.028047
2030 | 16 | 40.7161 | 1 | 0.92293 | 1339.8142 | 37.5781 | 37.5781 | 0.36455 | 13.699 | 13.699 | 0.028047 | 0.028047
2031 | 17 | 40.7161 | 1 | 0.91832 | 1333.1151 | 37.3902 | 37.3902 | 0.34227 | 12.7974 | 12.7974 | 0.028047 | 0.028047
2032 | 18 | 40.7161 | 1 | 0.91372 | 1326.4496 | 37.2033 | 37.2033 | 0.32135 | 11.9551 | 11.9551 | 0.028047 | 0.028047
2033 | 19 | 40.7161 | 1 | 0.90916 | 1319.8173 | 37.0173 | 37.0173 | 0.30171 | 11.1683 | 11.1683 | 0.028047 | 0.028047
2034 | 20 | 40.7161 | 1 | 0.90461 | 1313.2182 | 36.8322 | 36.8322 | 0.28326 | 10.4333 | 10.4333 | 0.028047 | 0.028047
2035 | 21 | 40.7161 | 1 | 0.90009 | 1306.6521 | 36.648 | 36.648 | 0.26595 | 9.7466 | 9.7466 | 0.028047 | 0.028047
2036 | 22 | 40.7161 | 1 | 0.89559 | 1300.1189 | 36.4648 | 36.4648 | 0.2497 | 9.1051 | 9.1051 | 0.028047 | 0.028047
2037 | 23 | 40.7161 | 1 | 0.89111 | 1293.6183 | 36.2824 | 36.2824 | 0.23443 | 8.5059 | 8.5059 | 0.028047 | 0.028047
2038 | 24 | 40.7161 | 1 | 0.88665 | 1287.1502 | 36.101 | 36.101 | 0.22011 | 7.946 | 7.946 | 0.028047 | 0.028047
[6 empty] | Validation: Present Value |  |  | 505.8541 | 505.8541
[5 empty] | Levelized cost: |  | 0.028047
**Avoided Transmission Capacity Coast
***(Example) Economic value of avoided transmission capacity cost
Avoided transmission costs are calculated the same way as avoided generation costs except in two
ways. First, transmission capacity is assumed not to degrade over time (PV degradation is still accounted
for). Second, avoided transmission capacity costs are calculated based on the utility’s 5-year average
MISO OATT Schedule 9 charge in Start Year USD, e.g., in 2014 USD if year one of the VOS tariff was
2014. Table 13 shows the example calculation.

## Table 14
|  | Year | Peak Load | Distribution Project Costs | Distribution Project Costs | Capacity Related | Capacity Related
|  |  | (kW) | ($) | (2014 $) | (% ) | (2014$) | 1.219
|  | 2004 | 6576559 | 105804117 | 128974628.2355 | 12.3% | 15863879.273 | 1.1951
|  | 2005 | 6379170 | 108039469 | 129117166.5198 | 11.3% | 14590239.8167
|  | 2006 | 6764087 | 105071496 | 123108003.9643 | 12% | 14772960.4757
|  | 2007 | 6567034 | 108937389 | 125134817.4154 | 12.1% | 15141312.9073
|  | 2008 | 6463488 | 138625404 | 156114720.3401 | 26.6% | 41526515.6105
|  | 2009 | 6410460 | 111965737 | 123619220.8378 | 13.9% | 17183071.6965
|  | 2010 | 6788458 | 129634955 | 140321044.3522 | 14.1% | 19785267.2537
|  | 2011 | 7221289 | 122977640 | 130504855.3891 | 14.9% | 19445223.453
|  | 2012 | 7194862 | 140736365 | 146422114.146 | 24.2% | 35434151.6233
|  | 2013 | 7283692 | 172580006 | 176031606.12 | 24.8% | 43655838.3178
237398460.4273
|  | AVG | 6764909.9 |  |  |  |  | 335.7197
|  | 9-year Load growth ((kW) |  |  | 707133
|  | Load growth rate (%/yr) |  |  | 1.141% | 5.587%
|  | Capacity-related Distribution Costs ($/kW) |  |  | 335.7197
|  | Distribution Capital Cost Escalation |  |  | 5.587%
**System-Wide Avoided Costs (FERC Accounts)
***(Example) Determination of deferrable costs
Avoided distribution capacity costs may be calculated in either of two ways:
System-wide Avoided Costs. These are calculated using utility-wide costs and lead to a VOS rate
that is “averaged” and applicable to all solar customers. This method is described below in the
methodology.
Location-specific Avoided Costs. These are calculated using location-specific costs, growth rates,
etc., and lead to location-specific VOS rates. This method provides the utility with a means for
offering a higher-value VOS rate in areas where capacity is most needed (areas of highest value).
The details of this method are site specific and not included in the methodology, however they
are to be implemented in accordance with the requirements set for the below.
System-wide Avoided Costs
System wide costs and peak growth rates are determined using actual data from each of the last 10
years. The costs and growth rate must be taken over the same time period because the historical
investments must be tied to the growth associated with those investments.
All costs for each year for FERC accounts 360, 361, 362, 365, 366, and 367 should be included. These
costs, however, should be adjusted to consider only capacity-related amounts. As such, the capacityrelated
percentages shown in Table 14 will be utility specific.
Cost per unit growth ($ per kW) is calculated by taking all of the total deferrable cost for each year,
adjusting for inflation, and dividing by the kW increase in peak annual load over the 10 years.
Future growth in peak load is assumed to be at the same rate as the last 10 years. It is calculated using
Equation 18 (p. 35)
| GrowthRate = | [(P(10)/P(1))^0.1)] - 1
Table 14 is an illustration of how to break out “capacity-related” distribution costs. The Company would have data like this for the last 10 years and go through the data to derive a cost per unit growth.
The result of their analysis is reported in Table 5 ($200 per kW) and this is then used in Table 15. However, the $200 is only an example. There is no numerical linkage between the costs shown in Table
14 and the $200 per kW (the analysis would require additional data as described in the text, not shown).

## Table 15
Table 15. (EXAMPLE) Economic value of avoided distribution capacity cost, system-wide.
|  | Conventional Planning |  |  |  |  | Deferred Distribution Planning |  |  |  |  | Costs |  |  | Disc. Costs |  | Prices
Year | Analysis Period | Distribution cost | New Dist. Capacity | Capital Cost | Disc. Capital Cost | Amortized | Def. Dist. Capacity | Def. Capital Cost | Disc. Capital Cost | Amortized | p.u. PV Production | Utility | VOS | Discount Factor | Utility | VOS | Utility | VOS
|  | ($/kW) | (MW) | ($M) | ($M) | $M/yr | (MW) | ($M) | ($M) | $M/yr | (kWh) | ($) | ($) |  | ($) | ($) | ($) | ($)
2014 | 0 | 335.7197 | 83.1249 | 27.9067 | 27.9067 | 45.7496 |  |  |  | 43.8124 | 1451.6947 | 23.3046 | 22.0861 | 1 | 23.3046 | 22.0861 | 0.016053 | 0.015214
2015 | 1 | 342.4341 | 84.0735 | 28.7896 | 27.03 | 45.7496 | 83.1249 | 28.4648 | 26.725 | 43.8124 | 1444.4362 | 23.0417 | 21.9756 | 0.93888 | 21.6333 | 20.6325 | 0.015952 | 0.015214
2016 | 2 | 349.2827 | 85.0329 | 29.7005 | 26.1808 | 45.7496 | 84.0735 | 29.3654 | 25.8854 | 43.8124 | 1437.214 | 22.7817 | 21.8657 | 0.88149 | 20.0819 | 19.2745 | 0.015851 | 0.015214
2017 | 3 | 356.2684 | 86.0033 | 30.6403 | 25.3584 | 45.7496 | 85.0329 | 30.2946 | 25.0723 | 43.8124 | 1430.0279 | 22.5246 | 21.7564 | 0.82762 | 18.6418 | 18.006 | 0.015751 | 0.015214
2018 | 4 | 363.3938 | 86.9848 | 31.6097 | 24.5618 | 45.7496 | 86.0033 | 31.2531 | 24.2846 | 43.8124 | 1422.8778 | 22.2705 | 21.6476 | 0.77703 | 17.3049 | 16.8209 | 0.015652 | 0.015214
2019 | 5 | 370.6616 | 87.9775 | 32.6099 | 23.7902 | 45.7496 | 86.9848 | 32.2419 | 23.5217 | 43.8124 | 1415.7634 | 22.0192 | 21.5394 | 0.72954 | 16.0639 | 15.7138 | 0.015553 | 0.015214
2020 | 6 | 378.0749 | 88.9815 | 33.6417 | 23.0428 | 45.7496 | 87.9775 | 33.2621 | 22.7828 | 43.8124 | 1408.6846 | 21.7708 | 21.4317 | 0.68495 | 14.9118 | 14.6796 | 0.015455 | 0.015214
2021 | 7 | 385.6364 | 89.9969 | 34.7061 | 22.3189 | 45.7496 | 88.9815 | 34.3145 | 22.0671 | 43.8124 | 1401.6412 | 21.5251 | 21.3245 | 0.64308 | 13.8424 | 13.7135 | 0.015357 | 0.015214
2022 | 8 | 393.3491 | 91.024 | 35.8042 | 21.6178 | 45.7496 | 89.9969 | 35.4002 | 21.3739 | 43.8124 | 1394.633 | 21.2822 | 21.2179 | 0.60378 | 12.8497 | 12.8109 | 0.01526 | 0.015214
2023 | 9 | 401.2161 | 92.0627 | 36.9371 | 20.9387 | 45.7496 | 91.024 | 36.5203 | 20.7024 | 43.8124 | 1387.6598 | 21.0421 | 21.1118 | 0.56687 | 11.9282 | 11.9677 | 0.015164 | 0.015214
2024 | 10 | 409.2404 | 93.1134 | 38.1057 | 20.2809 | 45.7496 | 92.0627 | 37.6758 | 20.052 | 43.8124 | 1380.7215 | 20.8047 | 21.0063 | 0.53223 | 11.0728 | 11.1801 | 0.015068 | 0.015214
2025 | 11 | 417.4252 | 94.176 | 39.3114 | 19.6438 | 45.7496 | 93.1134 | 38.8679 | 19.4221 | 43.8124 | 1373.8179 | 20.5699 | 20.9012 | 0.4997 | 10.2787 | 10.4443 | 0.014973 | 0.015214
2026 | 12 | 425.7737 | 95.2507 | 40.5552 | 19.0267 | 45.7496 | 94.176 | 40.0977 | 18.812 | 43.8124 | 1366.9488 | 20.3379 | 20.7967 | 0.46915 | 9.5416 | 9.7569 | 0.014878 | 0.015214
2027 | 13 | 434.2892 | 96.3377 | 41.8384 | 18.4289 | 45.7496 | 95.2507 | 41.3664 | 18.221 | 43.8124 | 1360.1141 | 20.1084 | 20.6927 | 0.44048 | 8.8573 | 9.1147 | 0.014784 | 0.015214
2028 | 14 | 442.975 | 97.4371 | 43.1622 | 17.85 | 45.7496 | 96.3377 | 42.6752 | 17.6486 | 43.8124 | 1353.3135 | 19.8815 | 20.5893 | 0.41356 | 8.2221 | 8.5148 | 0.014691 | 0.015214
2029 | 15 | 451.8345 | 98.5491 | 44.5279 | 17.2892 | 45.7496 | 97.4371 | 44.0254 | 17.0942 | 43.8124 | 1346.5469 | 19.6572 | 20.4863 | 0.38828 | 7.6325 | 7.9544 | 0.014598 | 0.015214
2030 | 16 | 460.8712 | 99.6737 | 45.9367 | 16.7461 | 45.7496 | 98.5491 | 45.4184 | 16.5572 | 43.8124 | 1339.8142 | 19.4354 | 20.3839 | 0.36455 | 7.0851 | 7.4309 | 0.014506 | 0.015214
2031 | 17 | 470.0886 | 100.8112 | 47.3902 | 16.22 | 45.7496 | 99.6737 | 46.8555 | 16.037 | 43.8124 | 1333.1151 | 19.2161 | 20.282 | 0.34227 | 6.577 | 6.9418 | 0.014414 | 0.015214
2032 | 18 | 479.4904 | 101.9616 | 48.8896 | 15.7105 | 45.7496 | 100.8112 | 48.338 | 15.5332 | 43.8124 | 1326.4496 | 18.9993 | 20.1806 | 0.32135 | 6.1053 | 6.485 | 0.014323 | 0.015214
2033 | 19 | 489.0802 | 103.1252 | 50.4365 | 15.2169 | 45.7496 | 101.9616 | 49.8674 | 15.0453 | 43.8124 | 1319.8173 | 18.7849 | 20.0797 | 0.30171 | 5.6675 | 6.0581 | 0.014233 | 0.015214
2034 | 20 | 498.8618 | 104.3021 | 52.0323 | 14.7389 | 45.7496 | 103.1252 | 51.4452 | 14.5726 | 43.8124 | 1313.2182 | 18.5729 | 19.9793 | 0.28326 | 5.2611 | 5.6594 | 0.014143 | 0.015214
2035 | 21 | 508.839 | 105.4924 | 53.6786 | 14.2759 | 45.7496 | 104.3021 | 53.073 | 14.1148 | 43.8124 | 1306.6521 | 18.3634 | 19.8794 | 0.26595 | 4.8838 | 5.2869 | 0.014054 | 0.015214
2036 | 22 | 519.0158 | 106.6962 | 55.377 | 13.8274 | 45.7496 | 105.4924 | 54.7522 | 13.6714 | 43.8124 | 1300.1189 | 18.1562 | 19.78 | 0.2497 | 4.5335 | 4.939 | 0.013965 | 0.015214
2037 | 23 | 529.3961 | 107.9139 | 57.1292 | 13.393 | 45.7496 | 106.6962 | 56.4846 | 13.2419 | 43.8124 | 1293.6183 | 17.9513 | 19.6811 | 0.23443 | 4.2084 | 4.6139 | 0.013877 | 0.015214
2038 | 24 | 539.984 | 109.1454 | 58.9368 | 12.9723 | 45.7496 | 107.9139 | 58.2718 | 12.8259 | 43.8124 | 1287.1502 | 17.7488 | 19.5827 | 0.22011 | 3.9066 | 4.3103 | 0.013789 | 0.015214
2039 | 25 | 550.7837 |  |  |  |  | 109.1454 | 60.1155 | 12.423 |  |  |  |  | 0.20665
|  |  |  | SUM | 488.3665 |  |  | SUM | 467.6874 |  |  | Validation Present Value |  |  | 274.3959 | 274.3959
|  |  |  | PMT | 45.7496 |  |  | PMT | 43.8124
[11 empty] | Levelized Cost |  | 0.015214
** Avoided Disribution Capacity Costs
*** (Example) Economic value of avoided Distribution Planning
Avoided distribution capacity costs may be calculated in either of two ways:
System-wide Avoided Costs. These are calculated using utility-wide costs and lead to a VOS rate
that is “averaged” and applicable to all solar customers. This method is described below in the
methodology.
Location-specific Avoided Costs. These are calculated using location-specific costs, growth rates,
etc., and lead to location-specific VOS rates. This method provides the utility with a means for
offering a higher-value VOS rate in areas where capacity is most needed (areas of highest value).
The details of this method are site specific and not included in the methodology, however they
are to be implemented in accordance with the requirements set for the below.
System-wide Avoided Costs
System wide costs and peak growth rates are determined using actual data from each of the last 10
years. The costs and growth rate must be taken over the same time period because the historical
investments must be tied to the growth associated with those investments.
Future growth in peak load is assumed to be at the same rate as the last 10 years. It is calculated using
the ratio of peak loads of the most recent year (year 10) and the peak load from the earlier year (year 1):
Equation 18 (p. 35)
| GrowthRate = | [(P(10)/P(1))^0.1)] - 1
A sample economic value calculation is presented in Table 15. The distribution cost for the first year
($200 per kW in the example) is taken from the analysis of historical cost and growth as described
above. This cost is escalated each year using the rate in the VOS Data Table.
For each future year, the amount of new distribution capacity is calculated based on the growth rate,
and this is multiplied by the cost per kW to get the cost for the year. The total discounted cost is
calculated ($149M) and amortized over the 25 years.
PV is assumed to be installed in sufficient capacity to allow this investment stream to be deferred for
one year. The total discounted cost of the deferred time series is calculated ($140M) and amortized.
Utility costs are calculated using the difference between the amortized costs of the conventional plan
and the amortized cost of the deferred plan. For example, the utility cost for 2022 is ($14M -
$13M)/54MW x 1000 W/kW = $14 per effective kW of PV. As before, utility prices are back-calculated
using PV production, and the VOS component rate is calculated such that the total discounted amount
equals the discounted utility cost.
Note that this analysis uses past technical and cost data (adjusted to today’s dollars) and that this trend is assumed to continue over the next 25 years. So, we look back 10 years and forward 25 years.
The 10 years is looking back. We could have also used 25 years or some other period, but 10 years seems like a good sampling period.
Table 5 values, derived from the cost analysis above, are used in Tables 15-16. We use them to estimate capacity-related distribution capital costs over the next 25 years. For example,
peak load is 5000 MW, so the new capacity in the first year is 1% of this, or 50 MW. At $200 per kW, this is $10M. This is carried on for the remaining 25 years.
The growth rate of the peak load is calculated using equation 18.
As an alternative to system-wide costs for distribution, location-specific costs may be used. When
calculating location-specific costs, the calculation should follow the same method of the system-wide
avoided cost method, but use local technical and cost data. The calculation should satisfy the following
requirements:
1. The distribution cost VOS should be calculated for each distribution planning area, defined as
the minimum area in which capacity needs cannot be met by transferring loads internally from
one circuit to another.
2. Distribution loads (the sum of all relevant feeders), peak load growth rates and capital costs
should be based on the distribution planning area.
3. Local Fleet Production Shapes may be used, if desired. Alternatively, the system-level Fleet
Production Shape may be used.
4. Anticipated capital costs should be evaluated based on capacity related investments only (as
above) using budgetary engineering cost estimates. All anticipated capital investments in the
planning area should be included. Planned capital investments should be assumed to meet
capacity requirements for the number of years defined by the amount of new capacity added (in
MW) divided by the local growth rate (MW per year). Beyond this time period, which is beyond
the planning horizon, new capacity investments should be assumed each year using the systemwide
method.
5. Planning areas for which engineering cost estimates are not available may be combined, and the
VOS calculated using the system-wide method.

## Table 16
Table 16 Natutal Gas Emmission
NG Emissions lb/MMBtu
PM10 | 0.007
CO | 0.04
NOX | 0.092
pB | 0
CO2 | 117
p. 39 - CO2 and non-CO2 natural gas emissions factors (lb per MM BTU of natural gas) are
taken from the EPA and NaturalGas.org, both of which have nearly identical numbers for the
emissions factors. Avoided environmental costs are based on the federal social cost of CO2 emissions
plus the Minnesota PUC-established externality costs for non-CO2 emissions
http://www.epa.gov/climatechange/ghgemissions/ind-assumptions.html
http://www.epa.gov/ttnchie1/ap42/
http://www.naturalgas.org/environment/naturalgas.asp
See http://www.epa.gov/climatechange/EPAactivities/economics/scc.html, EPA technical document appendix,
May 2013.
“Notice of Updated Environmental Externality Values,” issued June 5, 2013, PUC docket numbers E-999/CI-93-
583 and E-999/CI-00-1636.
The externality cost of CO2 emissions shown in Table 4 are calculated as follows. The EPA Social Cost of
Carbon (CO2) estimated for a given year is published in 2007 dollars per metric ton. These costs are
adjusted for inflation (converted to current dollars), converted to dollars per short ton, and then
converted to cost per unit fuel consumption using the assumed values in Table 16.
For example, the EPA externality cost for 2020 (3.0% discount rate, average) is $43 per metric ton of CO2
emissions in 2007 dollars. This is converted to current dollars by multiplying by a CPI adjustment factor;
for 2014, the CPI adjustment factor is of 1.12. The resulting CO2 costs per metric ton in current dollars
are then converted to dollars per short ton by dividing by 1.102. Finally, the costs are escalated using the
general escalation rate of 2.53% per year to give $50.77 per ton. Which equates to $51.22 per ton of
CO2, divided by 2000 pounds per ton, and multiplied by 117.0 pounds of CO2 per MMBtu = $2.970 per
MMBtu in 2020 dollars.

## Table 17
Table 17. (EXAMPLE) Economic value of avoided environmental cost
[5 empty] | Prices |  | Costs |  |  | Disc. Costs
Year | Analysis Period | Env. Cost | Heat Rate | p.u. PV Production | Utility | VOS | Utility | VOS | Discount Factor | Utility | VOS
|  | ($/MMBtu) | (Btu/kWh) | (kWh) | ($) | ($) | ($) | ($) |  | ($) | ($)
2014 | 0 | 2.2606 | 6950.164 | 1451.6947 | 0.015712 | 0.026159 | 22.8086 | 37.9753 | 1 | 22.8086 | 37.9753
2015 | 1 | 2.3847 | 6957.1142 | 1444.4362 | 0.016591 | 0.026159 | 23.9642 | 37.7854 | 0.94489 | 22.6436 | 35.703
2016 | 2 | 2.5149 | 6964.0713 | 1437.214 | 0.017514 | 0.026159 | 25.171 | 37.5964 | 0.89282 | 22.4731 | 33.5667
2017 | 3 | 2.6493 | 6971.0354 | 1430.0279 | 0.018468 | 0.026159 | 26.4102 | 37.4085 | 0.84361 | 22.2799 | 31.5582
2018 | 4 | 2.7902 | 6978.0064 | 1422.8778 | 0.01947 | 0.026159 | 27.703 | 37.2214 | 0.79712 | 22.0826 | 29.6699
2019 | 5 | 3.005 | 6984.9844 | 1415.7634 | 0.02099 | 0.026159 | 29.7164 | 37.0353 | 0.75319 | 22.3821 | 27.8946
2020 | 6 | 3.1592 | 6991.9694 | 1408.6846 | 0.022089 | 0.026159 | 31.1168 | 36.8501 | 0.71168 | 22.1453 | 26.2256
2021 | 7 | 3.2464 | 6998.9614 | 1401.6412 | 0.022722 | 0.026159 | 31.8477 | 36.6659 | 0.67246 | 21.4163 | 24.6564
2022 | 8 | 3.4102 | 7005.9603 | 1394.633 | 0.023891 | 0.026159 | 33.3198 | 36.4826 | 0.6354 | 21.1714 | 23.181
2023 | 9 | 3.5824 | 7012.9663 | 1387.6598 | 0.025123 | 0.026159 | 34.8624 | 36.3001 | 0.60038 | 20.9308 | 21.794
2024 | 10 | 3.7594 | 7019.9793 | 1380.7215 | 0.026391 | 0.026159 | 36.4382 | 36.1186 | 0.5673 | 20.6712 | 20.49
2025 | 11 | 3.9443 | 7026.9992 | 1373.8179 | 0.027717 | 0.026159 | 38.0779 | 35.9381 | 0.53603 | 20.411 | 19.2639
2026 | 12 | 4.1366 | 7034.0262 | 1366.9488 | 0.029097 | 0.026159 | 39.7736 | 35.7584 | 0.50649 | 20.145 | 18.1113
2027 | 13 | 4.3373 | 7041.0603 | 1360.1141 | 0.030539 | 0.026159 | 41.5367 | 35.5796 | 0.47858 | 19.8785 | 17.0276
2028 | 14 | 4.5438 | 7048.1013 | 1353.3135 | 0.032025 | 0.026159 | 43.34 | 35.4017 | 0.4522 | 19.5985 | 16.0087
2029 | 15 | 4.7604 | 7055.1494 | 1346.5469 | 0.033585 | 0.026159 | 45.2238 | 35.2247 | 0.42728 | 19.3233 | 15.0509
2030 | 16 | 4.9843 | 7062.2046 | 1339.8142 | 0.0352 | 0.026159 | 47.1613 | 35.0485 | 0.40373 | 19.0406 | 14.1503
2031 | 17 | 5.1218 | 7069.2668 | 1333.1151 | 0.036208 | 0.026159 | 48.269 | 34.8733 | 0.38148 | 18.4138 | 13.3036
2032 | 18 | 5.3607 | 7076.336 | 1326.4496 | 0.037934 | 0.026159 | 50.3177 | 34.6989 | 0.36046 | 18.1375 | 12.5076
2033 | 19 | 5.6098 | 7083.4124 | 1319.8173 | 0.039736 | 0.026159 | 52.4447 | 34.5254 | 0.34059 | 17.8624 | 11.7592
2034 | 20 | 5.8684 | 7090.4958 | 1313.2182 | 0.04161 | 0.026159 | 54.6424 | 34.3528 | 0.32182 | 17.5853 | 11.0556
2035 | 21 | 6.1368 | 7097.5863 | 1306.6521 | 0.043557 | 0.026159 | 56.9132 | 34.181 | 0.30409 | 17.3067 | 10.3941
2036 | 22 | 6.4155 | 7104.6839 | 1300.1189 | 0.04558 | 0.026159 | 59.2593 | 34.0101 | 0.28733 | 17.027 | 9.7721
2037 | 23 | 6.7037 | 7111.7886 | 1293.6183 | 0.047675 | 0.026159 | 61.6738 | 33.8401 | 0.27149 | 16.7441 | 9.1874
2038 | 24 | 7.0049 | 7118.9003 | 1287.1502 | 0.049867 | 0.026159 | 64.1867 | 33.6709 | 0.25653 | 16.466 | 8.6377
[8 empty] | Validation: Present Value |  | 498.9445 | 498.9445
[5 empty] | Levelized Cost |  | 0.026159
The externality cost of CO2 emissions shown in Table 4 are calculated as follows. The EPA Social Cost of
Carbon (CO2) estimated for a given year is published in 2007 dollars per metric ton. These costs are
adjusted for inflation (converted to current dollars), converted to dollars per short ton, and then
converted to cost per unit fuel consumption using the assumed values in Table 16.
For example, the EPA externality cost for 2020 (3.0% discount rate, average) is $43 per metric ton of CO2
emissions in 2007 dollars. This is converted to current dollars by multiplying by a CPI adjustment factor;
for 2014, the CPI adjustment factor is of 1.12. The resulting CO2 costs per metric ton in current dollars
are then converted to dollars per short ton by dividing by 1.102. Finally, the costs are escalated using the
general escalation rate of 2.53% per year to give $50.77 per ton. Which equates to $51.22 per ton of
CO2, divided by 2000 pounds per ton, and multiplied by 117.0 pounds of CO2 per MMBtu = $2.970 per
MMBtu in 2020 dollars.
In the example shown in Table 17, the environmental cost is the sum of the costs of all pollutants. For
example, in 2020, the total cost of $3.052 per MMBtu corresponds to the 2020 total cost in Table 4. This
cost is multiplied by the heat rate for the year (see Avoided Fuel Cost calculation) and divided by 106 (to
convert Btus to MMBtus), which results in the environmental cost in dollars per kWh for each year. The
remainder of the calculation follows the same method as the avoided variable O&M costs but using the
environmental discount factor (see Discount Factors for a description of the environmental discount
factor and its calculation).